## 2019 CCP Summary
Date: | REV 0 July 29, 2019
Project No.: | 18106417
Subject: | Capital and O&M Cost Summary Table
Project Short Title: | Tyrone Mine Closure Closeout Plan
SUMMARY BY SYSTEM |  | SUMMARY BY CATEGORY
Indirect | Inputs | Cost Category | Cost | Indirect % | Indirect Cost | Total Cost
Capital Cost | 30% | Capital Cost | 11913245.1683 | 30% | 3573973.5505 | 15487218.7188
O&M Cost (commodities, labor routine maint, replacement) | 17.5% | O&M - Reagents | 93195668.3073 | 17.5% | 16309241.9538 | 109504910.2611
Capital Cost Elements | 2019 Tyrone CCP Update | O&M - Analytical | 1881204 | 17.5% | 329210.7 | 2210414.7
Short-Term Evaporative Treatment System (ETS) | 1331300 | O&M - Power | 36467276.6874 | 17.5% | 6381773.4203 | 42849050.1077
Long-Term ETS | 1257312 | O&M - Replacement O&M | 16821399.1295 | 17.5% | 2943744.8477 | 19765143.9772
Tyrone Water Treatment System (TTS) | 7232445.0003 | O&M - Routine Maintenance1 | 15411864.3664 | 17.5% | 2697076.2641 | 18108940.6305
Water Collection/Conveyance for TTS | 959861 | O&M - Labor | 100154135.286 | 17.5% | 17526973.675 | 117681108.961
Sludge Disposal Facility for TTS | 142304.818 | Total, Capital | 275844792.9449 |  | 49761994.4114 | 325606787.3563
Salt Disposal Facility for ETS | 990022.35
Subtotal, Capital | 11913245.1683
Indirect Costs, Capital | 3573973.5505
Total, Capital | 15487218.7188
O&M Costs - Commodities (Reagents, Analytical, Power)
Short-Term ETS | 17063018.5443
Long-Term ETS | 7559078.6871
Tyrone Water Treatment System (TTS) | 100303735.6607
Water Collection/Conveyance for TTS | 6618316.1026
Sludge Disposal Facility for TTS | 0
Salt Disposal Facility for ETS | 0
Subtotal, O&M Commodities | 131544148.9947
Indirect Costs, O&M Commodities | 23020226.0741
Total, O&M Commodities | 154564375.0688
O&M Costs - Replacement O&M, Routine Maintenance, Labor
Short-Term ETS | 1336899.1725
Long-Term ETS | 6351324.2174
Tyrone Water Treatment System (TTS) | 105570872.2707
Water Collection/Conveyance for TTS | 6633702.378
Sludge Disposal Facility for TTS | 5142345.7835
Salt Disposal Facility for ETS | 7352254.9599
Subtotal, Replacement O&M, Routine Maintenance, Labor | 132387398.7819
Indirect Costs, Replacement O&M, Routine Maintenance, Labor | 23167794.7868
Total, O&M Labor, Routine Maintenance | 155555193.5687
Total, O&M | 310119568.6375
Total, Capital and O&M in Current Costs | 325606787.3563

## 2019 CCP Cash Flow
[17 empty] | Indirect |  |  | Inputs
Date: |  | REV 0 July 29, 2019 | [14 empty] | Capital Cost |  |  | 30%
Project No.: |  | 18106417 | [14 empty] | O&M Cost (power, reagents, analytical) |  |  | 17.5%
Subject: |  | Summary Cash Flow in Current Costs | [14 empty] | O&M Cost (replacement O&M, labor, routine maintenance) |  |  | 17.5%
Project Short Title: |  | Tyrone Mine Closure Closeout Plan
Year | Short-Term ETS |  |  | Long-Term ETS |  |  | TTS |  |  | Water Conveyance |  |  | Sludge Disposal Facility |  | Salt Disposal Facility |  | Total
| Capital | Power | Replacement O&M, Routine Maintenance, Labor | Capital | Power | Replacement O&M, Routine Maintenance, Labor | Capital | Reagents, Analytical, Power | Replacement O&M, Routine Maintenance, Labor | Capital | Power | Replacement O&M, Routine Maintenance, Labor | Capital | Replacement O&M, Routine Maintenance, Labor | Capital | Replacement O&M, Routine Maintenance, Labor | Capital Cost Subtotal | Capital Cost Indirects | O&M Cost Subtotal (Reagents, Analytical, Power) | O&M Subtotal (Reagents, Analytical, Power) Indirects | O&M Subtotal (Replacement O&M, Routine Maintenance, Labor) | O&M Subtotal (Replacement O&M, Routine Maintenance, Labor) Indirects | Total Cost
0 | 1331300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1331300 | 399390 | 0 | 0 | 0 | 0 | 1730690
1 | 0 | 2570345.4185 | 148544.3525 | 0 | 0 | 0 | 0 | 3224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2573569.4185 | 450374.6482 | 148544.3525 | 25995.2617 | 3198483.6809
2 | 0 | 2741915.5819 | 148544.3525 | 0 | 0 | 0 | 0 | 3224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2745139.5819 | 480399.4268 | 148544.3525 | 25995.2617 | 3400078.6229
3 | 0 | 2476186.3674 | 148544.3525 | 0 | 0 | 0 | 0 | 3224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2479410.3674 | 433896.8143 | 148544.3525 | 25995.2617 | 3087846.7959
4 | 0 | 2209898.7721 | 148544.3525 | 0 | 0 | 0 | 0 | 3224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2213122.7721 | 387296.4851 | 148544.3525 | 25995.2617 | 2774958.8714
5 | 0 | 1942893.2585 | 148544.3525 | 0 | 0 | 0 | 0 | 3224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1946117.2585 | 340570.5202 | 148544.3525 | 25995.2617 | 2461227.3929
6 | 0 | 1675967.5136 | 148544.3525 | 0 | 0 | 0 | 0 | 3224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1679191.5136 | 293858.5149 | 148544.3525 | 25995.2617 | 2147589.6427
7 | 0 | 1415503.0328 | 148544.3525 | 0 | 0 | 0 | 0 | 3224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1418727.0328 | 248277.2307 | 148544.3525 | 25995.2617 | 1841543.8777
8 | 0 | 1148577.2879 | 148544.3525 | 0 | 0 | 0 | 0 | 3224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1151801.2879 | 201565.2254 | 148544.3525 | 25995.2617 | 1527906.1275
9 | 0 | 881731.3117 | 148544.3525 | 709540 | 0 | 0 | 0 | 3224 | 0 | 32000 | 0 | 0 | 0 | 0 | 990022.35 | 0 | 1731562.35 | 519468.705 | 884955.3117 | 154867.1796 | 148544.3525 | 25995.2617 | 3465393.1605
10 | 0 | 0 | 0 | 0 | 502203.3519 | 69794.7716 | 0 | 3224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 528543.2723 | 0 | 0 | 505427.3519 | 88449.7866 | 598338.0439 | 104709.1577 | 1296924.3401
11 | 0 | 0 | 0 | 0 | 501063.2288 | 69794.7716 | 0 | 3224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 443884.389 | 0 | 0 | 504287.2288 | 88250.265 | 513679.1606 | 89893.8531 | 1196110.5076
12 | 0 | 0 | 0 | 0 | 499925.5168 | 69794.7716 | 0 | 3224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360410.3377 | 0 | 0 | 503149.5168 | 88051.1654 | 430205.1093 | 75285.8941 | 1096691.6857
13 | 0 | 0 | 0 | 0 | 433823.0737 | 69794.7716 | 0 | 1612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265483.3404 | 0 | 0 | 435435.0737 | 76201.1379 | 335278.112 | 58673.6696 | 905587.9932
14 | 0 | 0 | 0 | 547772 | 425627.9707 | 69794.7716 | 7232445.0003 | 1612 | 0 | 927861 | 0 | 0 | 142304.818 | 0 | 0 | 187773.7778 | 8850382.8183 | 2655114.8455 | 427239.9707 | 74766.9949 | 257568.5494 | 45074.4961 | 12310147.6749
15 | 0 | 0 | 0 | 0 | 73991.9722 | 69794.7716 | 0 | 1461543.1878 | 1430816.425 | 0 | 87682.1101 | 77136.0742 | 0 | 75915.8104 | 0 | 79942.2959 | 0 | 0 | 1623217.2701 | 284063.0223 | 1733605.3771 | 303380.941 | 3944266.6104
16 | 0 | 0 | 0 | 0 | 73948.2347 | 69794.7716 | 0 | 1446858.1302 | 1430816.425 | 0 | 87152.3338 | 77136.0742 | 0 | 75089.2255 | 0 | 79031.2557 | 0 | 0 | 1607958.6987 | 281392.7723 | 1731867.752 | 303076.8566 | 3924296.0795
17 | 0 | 0 | 0 | 0 | 73904.4973 | 69794.7716 | 0 | 1432308.8114 | 1430816.425 | 0 | 86624.7182 | 77136.0742 | 0 | 74270.6351 | 0 | 78122.5819 | 0 | 0 | 1592838.0269 | 278746.6547 | 1730140.4878 | 302774.5854 | 3904499.7548
18 | 0 | 0 | 0 | 0 | 72083.9436 | 69794.7716 | 0 | 1417891.1269 | 1430816.425 | 0 | 86099.045 | 77136.0742 | 0 | 73459.8032 | 0 | 77216.1654 | 0 | 0 | 1576074.1155 | 275812.9702 | 1728423.2394 | 302474.0669 | 3882784.392
19 | 0 | 0 | 0 | 0 | 72040.2062 | 69794.7716 | 0 | 1403621.6687 | 1430816.425 | 0 | 85576.2068 | 77136.0742 | 0 | 72657.6643 | 0 | 76312.3932 | 0 | 0 | 1561238.0817 | 273216.6643 | 1726717.3283 | 302175.5325 | 3863347.6067
20 | 0 | 0 | 0 | 0 | 70219.6525 | 69794.7716 | 0 | 1389500.0801 | 1430816.425 | 0 | 85055.9929 | 77136.0742 | 0 | 71864.1763 | 0 | 75411.2318 | 0 | 0 | 1544775.7255 | 270335.752 | 1725022.6789 | 301878.9688 | 3842013.1252
21 | 0 | 0 | 0 | 0 | 70175.915 | 69794.7716 | 0 | 1375845.9879 | 1430816.425 | 0 | 84550.6385 | 77136.0742 | 0 | 71096.8804 | 0 | 74520.3147 | 0 | 0 | 1530572.5414 | 267850.1947 | 1723364.4659 | 301588.7815 | 3823375.9836
22 | 0 | 0 | 0 | 0 | 69243.7694 | 69794.7716 | 0 | 1363073.1435 | 1430816.425 | 0 | 84076.9011 | 77136.0742 | 0 | 70378.4692 | 0 | 73649.3538 | 0 | 0 | 1516393.8141 | 265368.9175 | 1721775.0938 | 301310.6414 | 3804848.4667
23 | 0 | 0 | 0 | 0 | 68311.6239 | 69794.7716 | 0 | 1351076.685 | 1430816.425 | 0 | 83631.7384 | 77136.0742 | 0 | 69703.1628 | 0 | 72795.9731 | 0 | 0 | 1503020.0473 | 263028.5083 | 1720246.4067 | 301043.1212 | 3787338.0834
24 | 0 | 0 | 0 | 0 | 68267.8864 | 69794.7716 | 0 | 1339787.2814 | 1430816.425 | 0 | 83212.6086 | 77136.0742 | 0 | 69067.1025 | 0 | 71958.5723 | 0 | 0 | 1491267.7765 | 260971.8609 | 1718772.9455 | 300785.2655 | 3771797.8484
25 | 0 | 0 | 0 | 0 | 67335.7409 | 69794.7716 | 0 | 1329089.177 | 1309432.1175 | 0 | 82815.4683 | 77136.0742 | 0 | 68463.9069 | 0 | 71134.4743 | 0 | 0 | 1479240.3862 | 258867.0676 | 1595961.3445 | 279293.2353 | 3613362.0336
26 | 0 | 0 | 0 | 0 | 66403.5953 | 69794.7716 | 0 | 1318926.1783 | 1309432.1175 | 0 | 82438.4488 | 77136.0742 | 0 | 67890.4887 | 0 | 70322.3844 | 0 | 0 | 1467768.2224 | 256859.4389 | 1594575.8364 | 279050.7714 | 3598254.2691
27 | 0 | 0 | 0 | 0 | 66359.8579 | 69794.7716 | 0 | 1309259.5827 | 1309432.1175 | 0 | 82080.1255 | 77136.0742 | 0 | 67344.7015 | 0 | 69521.4155 | 0 | 0 | 1457699.5661 | 255097.4241 | 1593229.0802 | 278815.089 | 3584841.1594
28 | 0 | 0 | 0 | 0 | 65427.7123 | 69794.7716 | 0 | 1300055.6208 | 1309432.1175 | 0 | 81739.4777 | 77136.0742 | 0 | 66824.6846 | 0 | 68730.7515 | 0 | 0 | 1447222.8108 | 253263.9919 | 1591918.3994 | 278585.7199 | 3570990.922
29 | 0 | 0 | 0 | 0 | 64495.5667 | 69794.7716 | 0 | 1291279.5365 | 1309432.1175 | 0 | 81415.0587 | 77136.0742 | 0 | 66328.4976 | 0 | 67949.652 | 0 | 0 | 1437190.1619 | 251508.2783 | 1590641.1128 | 278362.1947 | 3557701.7478
30 | 0 | 0 | 0 | 0 | 63563.4211 | 69794.7716 | 0 | 1282906.4028 | 1309432.1175 | 0 | 81106.1199 | 77136.0742 | 0 | 65854.7641 | 0 | 67177.5382 | 0 | 0 | 1427575.9439 | 249825.7902 | 1589395.2656 | 278144.1715 | 3544941.1712
31 | 0 | 0 | 0 | 0 | 63519.6837 | 69794.7716 | 0 | 1274892.8991 | 1309432.1175 | 0 | 80810.8579 | 77136.0742 | 0 | 65401.0752 | 0 | 66413.4499 | 0 | 0 | 1419223.4406 | 248364.1021 | 1588177.4883 | 277931.0605 | 3533696.0916
32 | 0 | 0 | 0 | 0 | 62587.5381 | 69794.7716 | 0 | 1267209.905 | 1309432.1175 | 0 | 80528.2255 | 77136.0742 | 0 | 64965.8171 | 0 | 65656.6795 | 0 | 0 | 1410325.6686 | 246806.992 | 1586985.4599 | 277722.4555 | 3521840.5759
33 | 0 | 0 | 0 | 0 | 62587.5381 | 69794.7716 | 0 | 1248148.8811 | 1309432.1175 | 0 | 80257.5289 | 77136.0742 | 0 | 64547.807 | 0 | 65503.4518 | 0 | 0 | 1390993.9481 | 243423.9409 | 1586414.2221 | 277622.4889 | 3498454.5999
34 | 0 | 0 | 0 | 0 | 62587.5381 | 69794.7716 | 0 | 1241052.3607 | 1309432.1175 | 0 | 79997.4584 | 77136.0742 | 0 | 64145.2916 | 0 | 65356.3924 | 0 | 0 | 1383637.3572 | 242136.5375 | 1585864.6472 | 277526.3133 | 3489164.8551
35 | 0 | 0 | 0 | 0 | 62587.5381 | 69794.7716 | 0 | 1234222.2374 | 1309432.1175 | 0 | 79747.6999 | 77136.0742 | 0 | 63757.654 | 0 | 65215.1908 | 0 | 0 | 1376557.4754 | 240897.5582 | 1585335.808 | 277433.7664 | 3480224.6081
36 | 0 | 0 | 0 | 0 | 61699.13 | 69794.7716 | 0 | 1227631.8049 | 1309432.1175 | 0 | 79507.3568 | 77136.0742 | 0 | 63383.4313 | 0 | 65079.2231 | 0 | 0 | 1368838.2917 | 239546.7011 | 1584825.6177 | 277344.4831 | 3470555.0936
37 | 0 | 0 | 0 | 0 | 61699.13 | 69794.7716 | 0 | 1221262.9343 | 1309432.1175 | 0 | 79275.4778 | 77136.0742 | 0 | 63021.5937 | 0 | 64948.1528 | 0 | 0 | 1362237.5422 | 238391.5699 | 1584332.7098 | 277258.2242 | 3462220.0461
38 | 0 | 0 | 0 | 0 | 61699.13 | 69794.7716 | 0 | 1215105.563 | 1309432.1175 | 0 | 79051.8321 | 77136.0742 | 0 | 62671.5933 | 0 | 64821.7168 | 0 | 0 | 1355856.525 | 237274.8919 | 1583856.2733 | 277174.8478 | 3454162.5381
39 | 0 | 0 | 0 | 0 | 61699.13 | 69794.7716 | 0 | 1209143.8233 | 1309432.1175 | 0 | 78835.74 | 77136.0742 | 0 | 62332.5432 | 0 | 64699.5774 | 0 | 0 | 1349678.6933 | 236193.7713 | 1583395.0839 | 277094.1397 | 3446361.6882
40 | 0 | 0 | 0 | 0 | 60810.7219 | 69794.7716 | 0 | 1203368.6614 | 1309432.1175 | 0 | 78626.8455 | 77136.0742 | 0 | 62003.9371 | 0 | 64581.5044 | 0 | 0 | 1342806.2288 | 234991.09 | 1582948.4048 | 277015.9708 | 3437761.6945
41 | 0 | 0 | 0 | 0 | 60810.7219 | 69794.7716 | 0 | 1197769.5001 | 1309432.1175 | 0 | 78424.8042 | 77136.0742 | 0 | 61685.1905 | 0 | 64467.2795 | 0 | 0 | 1337005.0261 | 233975.8796 | 1582515.4333 | 276940.2008 | 3430436.5399
42 | 0 | 0 | 0 | 0 | 60810.7219 | 69794.7716 | 0 | 1192339.5929 | 1188047.81 | 0 | 78229.4382 | 77136.0742 | 0 | 61375.9259 | 0 | 64356.7408 | 0 | 0 | 1331379.7529 | 232991.4568 | 1460711.3224 | 255624.4814 | 3280707.0136
43 | 0 | 0 | 0 | 0 | 60810.7219 | 69794.7716 | 0 | 1187070.2472 | 1188047.81 | 0 | 78040.1525 | 77136.0742 | 0 | 61075.6477 | 0 | 64249.7095 | 0 | 0 | 1325921.1215 | 232036.1963 | 1460304.0129 | 255553.2023 | 3273814.533
44 | 0 | 0 | 0 | 0 | 60810.7219 | 69794.7716 | 0 | 1181955.0555 | 1188047.81 | 0 | 77856.8402 | 77136.0742 | 0 | 60784.0056 | 0 | 64146.0642 | 0 | 0 | 1320622.6176 | 231108.9581 | 1459908.7256 | 255484.027 | 3267124.3283
45 | 0 | 0 | 0 | 0 | 60810.7219 | 69794.7716 | 0 | 1176985.868 | 1188047.81 | 0 | 77679.1507 | 77136.0742 | 0 | 60500.5389 | 0 | 64045.6039 | 0 | 0 | 1315475.7406 | 230208.2546 | 1459524.7986 | 255416.8398 | 3260625.6336
46 | 0 | 0 | 0 | 0 | 59922.3138 | 69794.7716 | 0 | 1172152.5161 | 1188047.81 | 0 | 77506.6803 | 77136.0742 | 0 | 60224.6893 | 0 | 63948.0788 | 0 | 0 | 1309581.5102 | 229176.7643 | 1459151.4239 | 255351.4992 | 3253261.1976
47 | 0 | 0 | 0 | 0 | 59922.3138 | 69794.7716 | 0 | 1167455.1117 | 1188047.81 | 0 | 77339.5766 | 77136.0742 | 0 | 59956.4568 | 0 | 63853.5489 | 0 | 0 | 1304717.002 | 228325.4754 | 1458788.6615 | 255288.0158 | 3247119.1547
48 | 0 | 0 | 0 | 0 | 59922.3138 | 69794.7716 | 0 | 1162872.5613 | 1188047.81 | 0 | 77176.8394 | 77136.0742 | 0 | 59694.6762 | 0 | 63761.4834 | 0 | 0 | 1299971.7145 | 227495.05 | 1458434.8154 | 255226.0927 | 3241127.6726
49 | 0 | 0 | 0 | 0 | 59922.3138 | 69794.7716 | 0 | 1158410.4674 | 1188047.81 | 0 | 77018.7934 | 77136.0742 | 0 | 59439.6499 | 0 | 63672.0207 | 0 | 0 | 1295351.5745 | 226686.5255 | 1458090.3264 | 255165.8071 | 3235294.2335
50 | 0 | 0 | 0 | 0 | 59922.3138 | 69794.7716 | 0 | 1152588.2155 | 1188047.81 | 0 | 76798.3119 | 77136.0742 | 0 | 59111.246 | 0 | 63548.49 | 0 | 0 | 1289308.8411 | 225629.0472 | 1457638.3918 | 255086.7186 | 3227662.9986
51 | 0 | 0 | 0 | 0 | 59033.9056 | 69794.7716 | 0 | 1146385.4372 | 1188047.81 | 0 | 76382.1979 | 77136.0742 | 0 | 58824.7826 | 0 | 63317.4059 | 0 | 0 | 1281801.5407 | 224315.2696 | 1457120.8443 | 254996.1478 | 3218233.8025
52 | 0 | 0 | 0 | 0 | 59033.9056 | 69794.7716 | 0 | 1142954.1813 | 1188047.81 | 0 | 76240.8631 | 77136.0742 | 0 | 58634.7319 | 0 | 63239.13 | 0 | 0 | 1278228.9501 | 223690.0663 | 1456852.5177 | 254949.1906 | 3213720.7247
53 | 0 | 0 | 0 | 0 | 59033.9056 | 69794.7716 | 0 | 1139609.2326 | 1188047.81 | 0 | 76103.1629 | 77136.0742 | 0 | 58449.4367 | 0 | 63162.8466 | 0 | 0 | 1274746.3011 | 223080.6027 | 1456590.9391 | 254903.4143 | 3209321.2572
54 | 0 | 0 | 0 | 0 | 59033.9056 | 69794.7716 | 0 | 1136351.1628 | 1188047.81 | 0 | 75969.2202 | 77136.0742 | 0 | 58268.9324 | 0 | 63088.5752 | 0 | 0 | 1271354.2886 | 222487.0005 | 1456336.1634 | 254858.8286 | 3205036.2812
55 | 0 | 0 | 0 | 0 | 59033.9056 | 69794.7716 | 0 | 1133174.9892 | 1188047.81 | 0 | 75838.5844 | 77136.0742 | 0 | 58092.9321 | 0 | 63016.2354 | 0 | 0 | 1268047.4793 | 221908.3089 | 1456087.8233 | 254815.3691 | 3200858.9806
56 | 0 | 0 | 0 | 0 | 59033.9056 | 69794.7716 | 0 | 1130077.325 | 1188047.81 | 0 | 75711.2443 | 77136.0742 | 0 | 57921.2571 | 0 | 62945.7285 | 0 | 0 | 1264822.4749 | 221343.9331 | 1455845.6415 | 254772.9873 | 3196785.0367
57 | 0 | 0 | 0 | 0 | 59033.9056 | 69794.7716 | 0 | 1127058.7391 | 1188047.81 | 0 | 75587.2296 | 77136.0742 | 0 | 57753.9311 | 0 | 62877.0485 | 0 | 0 | 1261679.8743 | 220793.978 | 1455609.6354 | 254731.6862 | 3192815.1739
58 | 0 | 0 | 0 | 0 | 58145.4975 | 69794.7716 | 0 | 1124112.2856 | 1188047.81 | 0 | 75466.1161 | 77136.0742 | 0 | 57590.579 | 0 | 62810.0767 | 0 | 0 | 1257723.8992 | 220101.6824 | 1455379.3115 | 254691.3795 | 3187896.2725
59 | 0 | 0 | 0 | 0 | 58145.4975 | 69794.7716 | 0 | 1121236.3805 | 1188047.81 | 0 | 75348.2154 | 77136.0742 | 0 | 57431.1181 | 0 | 62744.731 | 0 | 0 | 1254730.0935 | 219577.7664 | 1455154.5048 | 254652.0383 | 3184114.4031
60 | 0 | 0 | 0 | 0 | 58145.4975 | 69794.7716 | 0 | 1118436.2588 | 1188047.81 | 0 | 75233.409 | 77136.0742 | 0 | 57275.8347 | 0 | 62681.1245 | 0 | 0 | 1251815.1653 | 219067.6539 | 1454935.615 | 254613.7326 | 3180432.1668
61 | 0 | 0 | 0 | 0 | 58145.4975 | 69794.7716 | 0 | 1115694.2859 | 1188047.81 | 0 | 75120.8667 | 77136.0742 | 0 | 57123.7484 | 0 | 62618.9126 | 0 | 0 | 1248960.6501 | 218568.1138 | 1454721.3168 | 254576.2304 | 3176826.3111
62 | 0 | 0 | 0 | 0 | 58145.4975 | 69794.7716 | 0 | 1113020.0966 | 1188047.81 | 0 | 75011.4165 | 77136.0742 | 0 | 56975.3989 | 0 | 62558.2568 | 0 | 0 | 1246177.0106 | 218080.9769 | 1454512.3115 | 254539.6545 | 3173309.9535
63 | 0 | 0 | 0 | 0 | 58145.4975 | 69794.7716 | 0 | 1110407.7035 | 1188047.81 | 0 | 74904.5349 | 77136.0742 | 0 | 56830.4632 | 0 | 62499.0193 | 0 | 0 | 1243457.7359 | 217605.1038 | 1454308.1382 | 254503.9242 | 3169874.9021
64 | 0 | 0 | 0 | 0 | 58145.4975 | 69794.7716 | 0 | 1107850.4366 | 1188047.81 | 0 | 74799.7924 | 77136.0742 | 0 | 56688.5458 | 0 | 62441.1176 | 0 | 0 | 1240795.7265 | 217139.2521 | 1454108.3192 | 254468.9559 | 3166512.2537
65 | 0 | 0 | 0 | 0 | 58145.4975 | 69794.7716 | 0 | 1105355.9666 | 1188047.81 | 0 | 74697.861 | 77136.0742 | 0 | 56550.1063 | 0 | 62384.6329 | 0 | 0 | 1238199.3251 | 216684.8819 | 1453913.395 | 254434.8441 | 3163232.4462
66 | 0 | 0 | 0 | 0 | 58145.4975 | 69794.7716 | 0 | 1102918.6713 | 1188047.81 | 0 | 74598.3062 | 77136.0742 | 0 | 56414.805 | 0 | 62329.4976 | 0 | 0 | 1235662.475 | 216240.9331 | 1453722.9584 | 254401.5177 | 3160027.8843
67 | 0 | 0 | 0 | 0 | 57257.0894 | 69794.7716 | 0 | 1100531.5394 | 1188047.81 | 0 | 74500.9045 | 77136.0742 | 0 | 56282.2801 | 0 | 62275.5218 | 0 | 0 | 1232289.5334 | 215650.6683 | 1453536.4577 | 254368.8801 | 3155845.5395
68 | 0 | 0 | 0 | 0 | 57257.0894 | 69794.7716 | 0 | 1098190.3248 | 1188047.81 | 0 | 74405.3924 | 77136.0742 | 0 | 56152.2734 | 0 | 62222.6204 | 0 | 0 | 1229852.8066 | 215224.2412 | 1453353.5496 | 254336.8712 | 3152767.4685
69 | 0 | 0 | 0 | 0 | 57257.0894 | 69794.7716 | 0 | 1095905.1687 | 1188047.81 | 0 | 74312.251 | 77136.0742 | 0 | 56025.3642 | 0 | 62171.0204 | 0 | 0 | 1227474.5091 | 214808.0391 | 1453175.0404 | 254305.6321 | 3149763.2207
70 | 0 | 0 | 0 | 0 | 57257.0894 | 69794.7716 | 0 | 1093668.7219 | 1188047.81 | 0 | 74221.3229 | 77136.0742 | 0 | 55901.1374 | 0 | 62120.549 | 0 | 0 | 1225147.1341 | 214400.7485 | 1453000.3422 | 254275.0599 | 3146823.2847
71 | 0 | 0 | 0 | 0 | 57257.0894 | 69794.7716 | 0 | 1091481.4466 | 1188047.81 | 0 | 74132.3665 | 77136.0742 | 0 | 55779.613 | 0 | 62071.2382 | 0 | 0 | 1222870.9025 | 214002.4079 | 1452829.507 | 254245.1637 | 3143947.9812
72 | 0 | 0 | 0 | 0 | 57257.0894 | 69794.7716 | 0 | 1089336.1742 | 1188047.81 | 0 | 74045.2388 | 77136.0742 | 0 | 55660.3967 | 0 | 62022.8956 | 0 | 0 | 1220638.5023 | 213611.7379 | 1452661.9481 | 254215.8409 | 3141128.0292
73 | 0 | 0 | 0 | 0 | 57257.0894 | 69794.7716 | 0 | 1087243.6816 | 1188047.81 | 0 | 73960.0668 | 77136.0742 | 0 | 55544.061 | 0 | 61975.841 | 0 | 0 | 1218460.8378 | 213230.6466 | 1452498.5578 | 254187.2476 | 3138377.2899
74 | 0 | 0 | 0 | 0 | 57257.0894 | 69794.7716 | 0 | 1085339.4792 | 1188047.81 | 0 | 73888.2612 | 77136.0742 | 0 | 55436.1522 | 0 | 61936.2381 | 0 | 0 | 1216484.8298 | 212884.8452 | 1452351.0461 | 254161.4331 | 3135882.1541
75 | 0 | 0 | 0 | 0 | 57257.0894 | 69794.7716 | 0 | 1083477.7496 | 1188047.81 | 0 | 73818.2871 | 77136.0742 | 0 | 55330.5609 | 0 | 61897.6298 | 0 | 0 | 1214553.1261 | 212546.7971 | 1452206.8465 | 254136.1981 | 3133442.9678
76 | 0 | 0 | 0 | 0 | 57257.0894 | 69794.7716 | 0 | 1081642.6436 | 1188047.81 | 0 | 73749.5111 | 77136.0742 | 0 | 55226.4441 | 0 | 61859.6309 | 0 | 0 | 1212649.2441 | 212213.6177 | 1452064.7308 | 254111.3279 | 3131038.9206
77 | 0 | 0 | 0 | 0 | 57257.0894 | 69794.7716 | 0 | 1079842.8079 | 1188047.81 | 0 | 73682.3491 | 77136.0742 | 0 | 55124.2773 | 0 | 61822.4662 | 0 | 0 | 1210782.2463 | 211886.8931 | 1451925.3992 | 254086.9449 | 3128681.4836
78 | 0 | 0 | 0 | 0 | 57257.0894 | 69794.7716 | 0 | 1078073.0067 | 1188047.81 | 0 | 73616.4907 | 77136.0742 | 0 | 55023.7687 | 0 | 61785.9662 | 0 | 0 | 1208946.5868 | 211565.6527 | 1451788.3907 | 254062.9684 | 3126363.5986
79 | 0 | 0 | 0 | 0 | 57257.0894 | 69794.7716 | 0 | 1076330.7983 | 1188047.81 | 0 | 73551.8502 | 77136.0742 | 0 | 54924.7854 | 0 | 61750.1197 | 0 | 0 | 1207139.7379 | 211249.4541 | 1451653.5609 | 254039.3732 | 3124082.126
80 | 0 | 0 | 0 | 0 | 57257.0894 | 69794.7716 | 0 | 1074614.6276 | 1188047.81 | 0 | 73488.3515 | 77136.0742 | 0 | 54827.2413 | 0 | 61714.8758 | 0 | 0 | 1205360.0685 | 210938.012 | 1451520.7729 | 254016.1353 | 3121834.9886
81 | 0 | 0 | 0 | 0 | 56368.6813 | 69794.7716 | 0 | 1072916.3602 | 1188047.81 | 0 | 73425.7075 | 77136.0742 | 0 | 54730.6943 | 0 | 61680.018 | 0 | 0 | 1202710.7489 | 210474.3811 | 1451389.3682 | 253993.1394 | 3118567.6376
82 | 0 | 0 | 0 | 0 | 56368.6813 | 69794.7716 | 0 | 1071242.2232 | 1188047.81 | 0 | 73364.0141 | 77136.0742 | 0 | 54635.4759 | 0 | 61645.7377 | 0 | 0 | 1200974.9186 | 210170.6107 | 1451259.8694 | 253970.4771 | 3116375.8758
83 | 0 | 0 | 0 | 0 | 56368.6813 | 69794.7716 | 0 | 1069596.6382 | 1188047.81 | 0 | 73303.6724 | 77136.0742 | 0 | 54541.8387 | 0 | 61612.0924 | 0 | 0 | 1199268.9918 | 209872.0736 | 1451132.587 | 253948.2027 | 3114221.8551
84 | 0 | 0 | 0 | 0 | 56368.6813 | 69794.7716 | 0 | 1067981.7123 | 1188047.81 | 0 | 73244.6299 | 77136.0742 | 0 | 54449.8903 | 0 | 61579.1758 | 0 | 0 | 1197595.0235 | 209579.1291 | 1451007.7218 | 253926.3513 | 3112108.2257
85 | 0 | 0 | 0 | 0 | 56368.6813 | 69794.7716 | 0 | 1066381.9565 | 1188047.81 | 0 | 73186.2064 | 77136.0742 | 0 | 54358.7819 | 0 | 61546.5957 | 0 | 0 | 1195936.8441 | 209288.9477 | 1450884.0334 | 253904.7058 | 3110014.5311
86 | 0 | 0 | 0 | 0 | 56368.6813 | 69794.7716 | 0 | 1064797.2825 | 1188047.81 | 0 | 73128.6339 | 77136.0742 | 0 | 54268.5209 | 0 | 61514.3464 | 0 | 0 | 1194294.5977 | 209001.5546 | 1450761.5231 | 253883.2665 | 3107940.942
87 | 0 | 0 | 0 | 0 | 56368.6813 | 69794.7716 | 0 | 1063244.5464 | 1188047.81 | 0 | 73072.3831 | 77136.0742 | 0 | 54180.016 | 0 | 61482.8312 | 0 | 0 | 1192685.6107 | 208719.9819 | 1450641.503 | 253862.263 | 3105909.3587
88 | 0 | 0 | 0 | 0 | 56368.6813 | 69794.7716 | 0 | 1061712.3165 | 1188047.81 | 0 | 73016.8013 | 77136.0742 | 0 | 54092.6329 | 0 | 61451.8416 | 0 | 0 | 1191097.7991 | 208442.1148 | 1450523.1304 | 253841.5478 | 3103904.5921
89 | 0 | 0 | 0 | 0 | 56368.6813 | 69794.7716 | 0 | 1060203.6141 | 1188047.81 | 0 | 72962.3525 | 77136.0742 | 0 | 54006.5542 | 0 | 61421.3476 | 0 | 0 | 1189534.6478 | 208168.5634 | 1450406.5576 | 253821.1476 | 3101930.9164
90 | 0 | 0 | 0 | 0 | 56368.6813 | 69794.7716 | 0 | 1058716.2855 | 1188047.81 | 0 | 72908.7912 | 77136.0742 | 0 | 53921.6537 | 0 | 61391.3666 | 0 | 0 | 1187993.7579 | 207898.9076 | 1450291.6762 | 253801.0433 | 3099985.385
91 | 0 | 0 | 0 | 0 | 56368.6813 | 69794.7716 | 0 | 1057251.1239 | 1188047.81 | 0 | 72856.2411 | 77136.0742 | 0 | 53837.9793 | 0 | 61361.8932 | 0 | 0 | 1186476.0462 | 207633.3081 | 1450178.5283 | 253781.2425 | 3098069.1251
92 | 0 | 0 | 0 | 0 | 56368.6813 | 69794.7716 | 0 | 1055812.7493 | 1066663.5025 | 0 | 72804.9456 | 77136.0742 | 0 | 53755.7856 | 0 | 61333.0376 | 0 | 0 | 1184986.3762 | 207372.6158 | 1328683.1714 | 232519.555 | 2953561.7184
93 | 0 | 0 | 0 | 0 | 56368.6813 | 69794.7716 | 0 | 1054397.2292 | 1066663.5025 | 0 | 72754.6359 | 77136.0742 | 0 | 53674.8519 | 0 | 61304.7238 | 0 | 0 | 1183520.5463 | 207116.0956 | 1328573.924 | 232500.4367 | 2951711.0027
94 | 0 | 0 | 0 | 0 | 56368.6813 | 69794.7716 | 0 | 1052993.2689 | 1066663.5025 | 0 | 72704.7606 | 77136.0742 | 0 | 53594.5572 | 0 | 61276.661 | 0 | 0 | 1182066.7108 | 206861.6744 | 1328465.5665 | 232481.4741 | 2949875.4259
95 | 0 | 0 | 0 | 0 | 56368.6813 | 69794.7716 | 0 | 1051617.0714 | 1066663.5025 | 0 | 72656.0619 | 77136.0742 | 0 | 53515.7894 | 0 | 61249.2455 | 0 | 0 | 1180641.8146 | 206612.3176 | 1328359.3832 | 232462.8921 | 2948076.4074
96 | 0 | 0 | 0 | 0 | 56368.6813 | 69794.7716 | 0 | 1050250.763 | 1066663.5025 | 0 | 72607.9322 | 77136.0742 | 0 | 53437.5794 | 0 | 61222.0484 | 0 | 0 | 1179227.3764 | 206364.7909 | 1328253.976 | 232444.4458 | 2946290.5891
97 | 0 | 0 | 0 | 0 | 56368.6813 | 69794.7716 | 0 | 1048905.3955 | 1066663.5025 | 0 | 72560.6276 | 77136.0742 | 0 | 53360.5198 | 0 | 61195.3407 | 0 | 0 | 1177834.7044 | 206121.0733 | 1328150.2088 | 232426.2865 | 2944532.2731
98 | 0 | 0 | 0 | 0 | 56368.6813 | 69794.7716 | 0 | 1047576.9083 | 1066663.5025 | 0 | 72513.9812 | 77136.0742 | 0 | 53284.3889 | 0 | 61169.0284 | 0 | 0 | 1176459.5708 | 205880.4249 | 1328047.7656 | 232408.359 | 2942796.1202
99 | 0 | 0 | 0 | 0 | 56368.6813 | 69794.7716 | 0 | 1046266.112 | 1066663.5025 | 0 | 72468.215 | 77136.0742 | 0 | 53209.2404 | 0 | 61143.1189 | 0 | 0 | 1175103.0083 | 205643.0264 | 1327946.7075 | 232390.6738 | 2941083.416
100 | 0 | 0 | 0 | 0 | 56368.6813 | 69794.7716 | 0 | 1044977.9742 | 1066663.5025 | 0 | 72423.2422 | 77136.0742 | 0 | 53135.33 | 0 | 61117.7278 | 0 | 0 | 1173769.8976 | 205409.7321 | 1327847.4061 | 232373.2961 | 2939400.3318
Total | 1331300 | 17063018.5443 | 1336899.1725 | 1257312 | 7559078.6871 | 6351324.2174 | 7232445.0003 | 100303735.6607 | 105570872.2707 | 959861 | 6618316.1026 | 6633702.378 | 142304.818 | 5142345.7835 | 990022.35 | 7352254.9599 | 11913245.1683 | 3573973.5505 | 131544148.9947 | 23020226.0741 | 132387398.7819 | 23167794.7868 | 325606787.3563
Notes:

## Short Term ETS Cash Flow 2019
Inputs
Date: |  | REV 0 July 29, 2019 |  |  |  |  | New Cost | 1331300
Project No.: |  | 18106417 |  |  |  |  | Replacement O&M Percentage | 0%
Subject: |  | Short Term ETS Direct Cost Cash Flow by Year in Current Cost Dollars |  |  |  |  | Routine Maintenance Percentage | 1.5%
Project Short Title: |  | Tyrone Mine Closure Closeout Plan |  |  |  |  | Avg ($/kWh) Year 1 through 14 | 0.044694
[7 empty] | Avg ($/kWh) Year 15 through 100 | 0.045334
Year Following Closure | Year | Capital | Replacement O&M1 | Routine Maintenance1 | O&M Labor | Annual Power Usage (kWh) | Electricity Annual Cost | Total Annual Cost
0 | 2014 | 1331300 | 0 | 0 | 0 | 0 | 0 | 1331300
1 | 2015 | 0 | 0 | 19969.5 | 128574.8525 | 57509400 | 2570345.4185 | 2718889.771
2 | 2016 | 0 | 0 | 19969.5 | 128574.8525 | 61348143.6513 | 2741915.5819 | 2890459.9344
3 | 2017 | 0 | 0 | 19969.5 | 128574.8525 | 55402667.3824 | 2476186.3674 | 2624730.7199
4 | 2018 | 0 | 0 | 19969.5 | 128574.8525 | 49444697.7937 | 2209898.7721 | 2358443.1246
5 | 2019 | 0 | 0 | 19969.5 | 128574.8525 | 43470665.3651 | 1942893.2585 | 2091437.611
6 | 2020 | 0 | 0 | 19969.5 | 128574.8525 | 37498417.6965 | 1675967.5136 | 1824511.8661
7 | 2021 | 0 | 0 | 19969.5 | 128574.8525 | 31670735.5865 | 1415503.0328 | 1564047.3853
8 | 2022 | 0 | 0 | 19969.5 | 128574.8525 | 25698487.9179 | 1148577.2879 | 1297121.6404
9 | 2023 | 0 | 0 | 19969.5 | 128574.8525 | 19728025.0093 | 881731.3117 | 1030275.6642
10 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 2028 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 2030 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2031 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 2032 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 2033 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 2034 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 2035 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 2036 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2038 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 2039 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 2040 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 2041 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 2042 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 2043 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 2044 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 2045 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 2046 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 2047 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 2048 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 2049 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 2050 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 2051 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 2052 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 2053 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 2054 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 2055 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 2056 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 2057 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 2058 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 2059 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 2060 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 2061 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 2062 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 2063 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 2064 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 2065 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 2066 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 2067 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 2068 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 2069 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 2070 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 2071 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 2072 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 2073 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | 2074 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 2075 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 2076 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 2077 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 2078 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | 2079 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 2080 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 2081 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 2082 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 2083 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 2084 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 2085 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 2086 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 2087 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 2088 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | 2089 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 2090 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 2091 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | 2092 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | 2093 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 2094 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | 2095 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | 2096 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | 2097 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | 2098 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | 2099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 2100 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 2101 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 2102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 2103 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 2104 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 2105 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 2106 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | 2107 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | 2108 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | 2109 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | 2110 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 2111 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 2112 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 2113 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 2114 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total |  | 1331300 | 0 | 179725.5 | 1157173.6725 | 381771240.4026 | 17063018.5443 | 19731217.7168
Notes:
1 Replacement O&M allowance for the Short-Term ETS is estimated at zero given this is a short-term system and capital replacement is not expected. Routine maintenance is estimated at a percentage of the initial direct capital cost (New Cost in Column H Row 4).
Cost estimate backup details are included in Attachment B to the Tyrone Water Treatment Cost Basis Document.
Costs do not include indirect costs

## Short Term ETS Labor 2019
Date: | REV 0 July 29, 2019
Project No.: | 18106417
Subject: | Labor Cost Estimate - ETS and Salt Disposal Facility Operations
Project Short Title: | Tyrone Mine Closure Closeout Plan
Short-Term ETS
Day shift - 1.5 operator (7 day/wk shift coverage)1
Operators | 1.5 | FTE
Operator Rate2 | 18.6 | /hr
Operator Hours (1 FTE) | 2087 | hr/yr
Operator Total Cost | 58227.3
Sub-Total Operator Cost | 58227.3
Overtime for operators | 15%
Total overtime hours for operators | 469.575 | hr/yr
Operator Overtime Total Cost | 13101.1425
Overtime Cost | 13101.1425
Supervisor | 0.5 | FTE
Supervisor Rate3 | 31.1 | /hr
Supervisor Hours (1 FTE) | 2087 | hr/yr
Supervisor Total Cost | 32452.85
Benefits fringe rate per hour4 | 5.94 | /hr
Total eligible hours per year | 4174 | hrs/yr
Benefits Cost | 24793.56
Benefits Cost | 24793.56
Total Operator Labor Cost | 128574.8525
Notes:
1 Operator numbers are estimated from Golder's experience with operating similar plants.
2 Wages from 2019 New Mexico Type "A" Street, Highway, Utility & Light Engineering Prevailing Wages. Operator Group I. https://www.dws.state.nm.us/Portals/0/DM/LaborRelations/Prevailing_Wage_Poster_A_2019_final.pdf
3 Wages from 2019 New Mexico Type "A" Street, Highway, Utility & Light Engineering Prevailing Wages. Operator Group X. https://www.dws.state.nm.us/Portals/0/DM/LaborRelations/Prevailing_Wage_Poster_A_2019_final.pdf
4 Wages from 2019 New Mexico Type "A" Street, Highway, Utility & Light Engineering Prevailing Wages. Operator Group I-X. https://www.dws.state.nm.us/Portals/0/DM/LaborRelations/Prevailing_Wage_Poster_A_2019_final.pdf
Costs do not include indirect costs

## Long Term ETS Cash Flow 2019
Inputs
[12 empty] | Total Pumps and Pipeline Costs if New | 712270
Date: |  | REV 0 July 29, 2019 | [9 empty] | Total Sprayer Costs if New | 227010
Project No.: |  | 18106417 | [9 empty] | Total Tank and Reservoir Cost if New | 1175713.0794
Subject: |  | Long Term ETS Direct Cost Cash Flow by Year in Current Cost Dollars | [9 empty] | Replacement O&M | 1.8%
Project Short Title: |  | Tyrone Mine Closure Closeout Plan | [9 empty] | Routine Maintenance Percentage | 1.5%
[12 empty] | Avg ($/kWh) Year 1 through 14 | 0.044694
[12 empty] | Avg ($/kWh) Year 15 through 100 | 0.045334
Year Following Closure | Year | Capital | Pumps and Pipeline Replacement O&M1 | Sprayers Replacement O&M1 | Tank and Reservoirs Replacement O&M1 | Pumps and Pipeline Routine Maintenance2 | Sprayers Routine Maintenance2 | Tank and Reservoirs Routine Maintenance2 | O&M Labor3 | Pumping System Annual Power Usage (kWh) | Mechanical Spray System Annual Power Usage (kWh) | Electricity Annual Cost | Total Annual Cost
1 | 2015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2023 | 709540 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 709540
10 | 2024 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 1437895.8479 | 9798498 | 502203.3519 | 571998.1235
11 | 2025 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 1412386.5156 | 9798498 | 501063.2288 | 570858.0004
12 | 2026 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 1386931.1299 | 9798498 | 499925.5168 | 569720.2885
13 | 2027 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 1318926.1366 | 8387514.288 | 433823.0737 | 503617.8453
14 | 2028 | 547772 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 1292343.302 | 8230738.32 | 425627.9707 | 1043194.7423
15 | 2029 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 64396.0146 | 1567759.68 | 73991.9722 | 143786.7438
16 | 2030 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 63431.23 | 1567759.68 | 73948.2347 | 143743.0064
17 | 2031 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 62466.4454 | 1567759.68 | 73904.4973 | 143699.2689
18 | 2032 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 61501.6608 | 1528565.688 | 72083.9436 | 141878.7152
19 | 2033 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 60536.8762 | 1528565.688 | 72040.2062 | 141834.9778
20 | 2034 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 59572.0916 | 1489371.696 | 70219.6525 | 140014.4241
21 | 2035 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 58607.307 | 1489371.696 | 70175.915 | 139970.6866
22 | 2036 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 57642.5224 | 1469774.7 | 69243.7694 | 139038.5411
23 | 2037 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 56677.7378 | 1450177.704 | 68311.6239 | 138106.3955
24 | 2038 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 55712.9532 | 1450177.704 | 68267.8864 | 138062.6581
25 | 2039 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 54748.1686 | 1430580.708 | 67335.7409 | 137130.5125
26 | 2040 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 53783.3839 | 1410983.712 | 66403.5953 | 136198.3669
27 | 2041 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 52818.5993 | 1410983.712 | 66359.8579 | 136154.6295
28 | 2042 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 51853.8147 | 1391386.716 | 65427.7123 | 135222.4839
29 | 2043 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 50889.0301 | 1371789.72 | 64495.5667 | 134290.3383
30 | 2044 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 49924.2455 | 1352192.724 | 63563.4211 | 133358.1928
31 | 2045 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 48959.4609 | 1352192.724 | 63519.6837 | 133314.4553
32 | 2046 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1332595.728 | 62587.5381 | 132382.3098
33 | 2047 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1332595.728 | 62587.5381 | 132382.3098
34 | 2048 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1332595.728 | 62587.5381 | 132382.3098
35 | 2049 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1332595.728 | 62587.5381 | 132382.3098
36 | 2050 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1312998.732 | 61699.13 | 131493.9016
37 | 2051 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1312998.732 | 61699.13 | 131493.9016
38 | 2052 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1312998.732 | 61699.13 | 131493.9016
39 | 2053 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1312998.732 | 61699.13 | 131493.9016
40 | 2054 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1293401.736 | 60810.7219 | 130605.4935
41 | 2055 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1293401.736 | 60810.7219 | 130605.4935
42 | 2056 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1293401.736 | 60810.7219 | 130605.4935
43 | 2057 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1293401.736 | 60810.7219 | 130605.4935
44 | 2058 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1293401.736 | 60810.7219 | 130605.4935
45 | 2059 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1293401.736 | 60810.7219 | 130605.4935
46 | 2060 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1273804.74 | 59922.3138 | 129717.0854
47 | 2061 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1273804.74 | 59922.3138 | 129717.0854
48 | 2062 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1273804.74 | 59922.3138 | 129717.0854
49 | 2063 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1273804.74 | 59922.3138 | 129717.0854
50 | 2064 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1273804.74 | 59922.3138 | 129717.0854
51 | 2065 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1254207.744 | 59033.9056 | 128828.6773
52 | 2066 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1254207.744 | 59033.9056 | 128828.6773
53 | 2067 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1254207.744 | 59033.9056 | 128828.6773
54 | 2068 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1254207.744 | 59033.9056 | 128828.6773
55 | 2069 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1254207.744 | 59033.9056 | 128828.6773
56 | 2070 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1254207.744 | 59033.9056 | 128828.6773
57 | 2071 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1254207.744 | 59033.9056 | 128828.6773
58 | 2072 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1234610.748 | 58145.4975 | 127940.2691
59 | 2073 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1234610.748 | 58145.4975 | 127940.2691
60 | 2074 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1234610.748 | 58145.4975 | 127940.2691
61 | 2075 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1234610.748 | 58145.4975 | 127940.2691
62 | 2076 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1234610.748 | 58145.4975 | 127940.2691
63 | 2077 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1234610.748 | 58145.4975 | 127940.2691
64 | 2078 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1234610.748 | 58145.4975 | 127940.2691
65 | 2079 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1234610.748 | 58145.4975 | 127940.2691
66 | 2080 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1234610.748 | 58145.4975 | 127940.2691
67 | 2081 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1215013.752 | 57257.0894 | 127051.861
68 | 2082 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1215013.752 | 57257.0894 | 127051.861
69 | 2083 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1215013.752 | 57257.0894 | 127051.861
70 | 2084 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1215013.752 | 57257.0894 | 127051.861
71 | 2085 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1215013.752 | 57257.0894 | 127051.861
72 | 2086 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1215013.752 | 57257.0894 | 127051.861
73 | 2087 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1215013.752 | 57257.0894 | 127051.861
74 | 2088 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1215013.752 | 57257.0894 | 127051.861
75 | 2089 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1215013.752 | 57257.0894 | 127051.861
76 | 2090 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1215013.752 | 57257.0894 | 127051.861
77 | 2091 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1215013.752 | 57257.0894 | 127051.861
78 | 2092 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1215013.752 | 57257.0894 | 127051.861
79 | 2093 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1215013.752 | 57257.0894 | 127051.861
80 | 2094 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1215013.752 | 57257.0894 | 127051.861
81 | 2095 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1195416.756 | 56368.6813 | 126163.4529
82 | 2096 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1195416.756 | 56368.6813 | 126163.4529
83 | 2097 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1195416.756 | 56368.6813 | 126163.4529
84 | 2098 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1195416.756 | 56368.6813 | 126163.4529
85 | 2099 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1195416.756 | 56368.6813 | 126163.4529
86 | 2100 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1195416.756 | 56368.6813 | 126163.4529
87 | 2101 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1195416.756 | 56368.6813 | 126163.4529
88 | 2102 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1195416.756 | 56368.6813 | 126163.4529
89 | 2103 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1195416.756 | 56368.6813 | 126163.4529
90 | 2104 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1195416.756 | 56368.6813 | 126163.4529
91 | 2105 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1195416.756 | 56368.6813 | 126163.4529
92 | 2106 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1195416.756 | 56368.6813 | 126163.4529
93 | 2107 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1195416.756 | 56368.6813 | 126163.4529
94 | 2108 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1195416.756 | 56368.6813 | 126163.4529
95 | 2109 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1195416.756 | 56368.6813 | 126163.4529
96 | 2110 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1195416.756 | 56368.6813 | 126163.4529
97 | 2111 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1195416.756 | 56368.6813 | 126163.4529
98 | 2112 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1195416.756 | 56368.6813 | 126163.4529
99 | 2113 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1195416.756 | 56368.6813 | 126163.4529
100 | 2114 | 0 | 12820.86 | 4086.18 | 21162.8354 | 10684.05 | 3405.15 | 17635.6962 | Included in Total Operating Cost | 47994.6763 | 1195416.756 | 56368.6813 | 126163.4529
Total |  | 1257312 | 1166698.26 | 371842.38 | 1925818.024 | 972248.55 | 309868.65 | 1604848.3534 | 0 | 11123637.138 | 156364431.084 | 7559078.6871 | 15167714.9045
Notes:
1 Replacement O&M costs are estimated at 1.8% of the total capital cost for the complete long-term ETS (pumps, pipelines, tanks, reservoirs, and sprayers). A higher percentage of capital cost is estimated given that existing pumps, pipelines, tanks and reservoirs will be utilized initially up until their associated life expectancies are met and will require replacement sooner than if new equipment was utilized initially. The spray systems from the short-ter ETS will be utilized through Year 19. In Year 20, 4 new spray evaporation units will be purchased. A higher percentage capital cost is estimated to ensure conservatism and to align with existing existing pumps, pipelines, tanks and reservoirs O&M Replacement estimates.
2 Routine maintenance is estimated at 1.5% of the total capital cost for the complete long-term ETS (pumps, pipelines, tanks, reservoirs, and sprayers). Routine maintenance includes materials needed for preventative maintenance such as mechanical seals, lubricant, valve sleeves, fuses, etc.
3 O&M Labor for the ETS is included in the TTS Labor.
Cost estimate backup details are included in Attachment B to the Tyrone Water Treatment Cost Basis Document.
Costs do not include indirect costs
|  |  | 936838.5912 | 306488 | 2076693.7175 | 3320020.3087
144338.3553

## Salt Disposal Cash Flow 2019
Inputs
[6 empty] | New Cost | 990022.35
Date: |  | REV 0 July 29, 2019 |  |  |  | Replacement O&M | 0.25%
Project No.: |  | 18106417 |  |  |  | Salt Removal ($/CY) | 5.6327
Subject: |  | Salt Disposal Direct Cost Cash Flow by Year in Current Cost Dollars
Project Short Title: |  | Tyrone Mine Closure Closeout Plan
Year Following Closure | Year | Capital | Replacement O&M1 | Routine Maintenance2 | O&M Labor2 | Annual Salt Production/ Removal (cy/yr) | Total Operating Cost3
1 | 2015 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2016 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2017 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2018 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2019 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2022 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2023 | 990022.35 | 0 | 0 | 0 | 0 | 990022.35
10 | 2024 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 93395.5999 | 528543.2723
11 | 2025 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 78365.6724 | 443884.389
12 | 2026 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 63546.0941 | 360410.3377
13 | 2027 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 46693.2154 | 265483.3404
14 | 2028 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 32897.0365 | 187773.7778
15 | 2029 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 13753.1581 | 79942.2959
16 | 2030 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 13591.4165 | 79031.2557
17 | 2031 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 13430.0949 | 78122.5819
18 | 2032 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 13269.1741 | 77216.1654
19 | 2033 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 13108.7228 | 76312.3932
20 | 2034 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 12948.735 | 75411.2318
21 | 2035 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 12790.5659 | 74520.3147
22 | 2036 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 12635.9397 | 73649.3538
23 | 2037 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 12484.4346 | 72795.9731
24 | 2038 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 12335.7665 | 71958.5723
25 | 2039 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 12189.4602 | 71134.4743
26 | 2040 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 12045.2857 | 70322.3844
27 | 2041 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 11903.0855 | 69521.4155
28 | 2042 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 11762.7149 | 68730.7515
29 | 2043 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 11624.0423 | 67949.652
30 | 2044 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 11486.9649 | 67177.5382
31 | 2045 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 11351.3124 | 66413.4499
32 | 2046 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 11216.9591 | 65656.6795
33 | 2047 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 11189.7558 | 65503.4518
34 | 2048 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 11163.6475 | 65356.3924
35 | 2049 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 11138.5793 | 65215.1908
36 | 2050 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 11114.4402 | 65079.2231
37 | 2051 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 11091.1707 | 64948.1528
38 | 2052 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 11068.7238 | 64821.7168
39 | 2053 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 11047.0398 | 64699.5774
40 | 2054 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 11026.0777 | 64581.5044
41 | 2055 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 11005.7988 | 64467.2795
42 | 2056 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10986.1742 | 64356.7408
43 | 2057 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10967.1724 | 64249.7095
44 | 2058 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10948.7717 | 64146.0642
45 | 2059 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10930.9365 | 64045.6039
46 | 2060 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10913.6224 | 63948.0788
47 | 2061 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10896.84 | 63853.5489
48 | 2062 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10880.4951 | 63761.4834
49 | 2063 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10864.6124 | 63672.0207
50 | 2064 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10842.6813 | 63548.49
51 | 2065 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10801.6558 | 63317.4059
52 | 2066 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10787.759 | 63239.13
53 | 2067 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10774.2161 | 63162.8466
54 | 2068 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10761.0303 | 63088.5752
55 | 2069 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10748.1874 | 63016.2354
56 | 2070 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10735.67 | 62945.7285
57 | 2071 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10723.4768 | 62877.0485
58 | 2072 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10711.587 | 62810.0767
59 | 2073 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10699.9858 | 62744.731
60 | 2074 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10688.6935 | 62681.1245
61 | 2075 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10677.6487 | 62618.9126
62 | 2076 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10666.8801 | 62558.2568
63 | 2077 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10656.3634 | 62499.0193
64 | 2078 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10646.0838 | 62441.1176
65 | 2079 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10636.0558 | 62384.6329
66 | 2080 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10626.2673 | 62329.4976
67 | 2081 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10616.6847 | 62275.5218
68 | 2082 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10607.2928 | 62222.6204
69 | 2083 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10598.132 | 62171.0204
70 | 2084 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10589.1716 | 62120.549
71 | 2085 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10580.4172 | 62071.2382
72 | 2086 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10571.8347 | 62022.8956
73 | 2087 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10563.4808 | 61975.841
74 | 2088 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10556.4499 | 61936.2381
75 | 2089 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10549.5956 | 61897.6298
76 | 2090 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10542.8495 | 61859.6309
77 | 2091 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10536.2514 | 61822.4662
78 | 2092 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10529.7714 | 61785.9662
79 | 2093 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10523.4074 | 61750.1197
80 | 2094 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10517.1503 | 61714.8758
81 | 2095 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10510.9619 | 61680.018
82 | 2096 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10504.8759 | 61645.7377
83 | 2097 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10498.9027 | 61612.0924
84 | 2098 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10493.0588 | 61579.1758
85 | 2099 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10487.2747 | 61546.5957
86 | 2100 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10481.5493 | 61514.3464
87 | 2101 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10475.9543 | 61482.8312
88 | 2102 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10470.4525 | 61451.8416
89 | 2103 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10465.0388 | 61421.3476
90 | 2104 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10459.7161 | 61391.3666
91 | 2105 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10454.4835 | 61361.8932
92 | 2106 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10449.3606 | 61333.0376
93 | 2107 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10444.3339 | 61304.7238
94 | 2108 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10439.3518 | 61276.661
95 | 2109 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10434.4846 | 61249.2455
96 | 2110 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10429.6561 | 61222.0484
97 | 2111 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10424.9146 | 61195.3407
98 | 2112 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10420.2432 | 61169.0284
99 | 2113 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10415.6434 | 61143.1189
100 | 2114 | 0 | 2475.0559 | Included in Total Operating Cost | Included in Total Operating Cost | 10411.1356 | 61117.7278
Total |  | 990022.35 | 225230.0846 | 0 | 0 | 1265297.4334 | 8342277.3099
Notes:
1 Replacement O&M is estimated only at 0.25% of the total capital cost since the capital cost of the facility is high since it is a lined facility. Costs associated with closure of each of the four individual cells comprising the salt disposal facility (approximately 316,324 cubic yards per cell). Closure includes grading, three foot of earthen cover, and revegetation. Initial capital cost for construction of salt disposal facility (by RS Means) shown in Year 9.
2 Routine Maintenance and O&M Labor is included in the Total Operating Cost calculation.
3 Costs based on 2019 RS Means estimate of $5.63 per/cy for excavation, loading, hauling, and placing of salts at the salt disposal facility.
Cost estimate backup details are included in Attachment B to the Tyrone Water Treatment Cost Basis Document.
Costs do not include indirect costs
80520

## Water Conveyance Cash Flow 2019
Inputs
[9 empty] | Total Pump and Pipeline Costs if New | 1895029.939
Date: |  | REV 0 July 29, 2019 | [6 empty] | Total Tank and Reservoir Cost if New | 442426.8538
Project No.: |  | 18106417 | [6 empty] | Replacement O&M Percentage | 1.8%
Subject: |  | Water Conveyance Direct Cost Cash Flow by Year in Current Cost Dollars | [6 empty] | Routine Maintenance Percentage | 1.5%
Project Short Title: |  | Tyrone Mine Closure Closeout Plan | [6 empty] | Avg ($/kWh) Year 1 through 14 | 0.044694
[9 empty] | Avg ($/kWh) Year 15 through 100 | 0.045334
Year Following Closure | Year | Capital1 | Pumps and Pipeline Replacement O&M2 | Tanks and Reservoir Replacement O&M2 | Pumps and Pipeline Routine Maintenance3 | Tanks and Reservoir Routine Maintenance3 | O&M Labor4 | Pumping System Annual Power Usage (kWh) | O&M Electrical Annual Cost | Total Annual Cost
1 | 2019 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0
2 | 2020 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0
3 | 2021 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0
4 | 2022 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0
5 | 2023 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0
6 | 2024 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0
7 | 2025 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0
8 | 2026 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0
9 5 | 2027 | 32000 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 32000
10 5 | 2028 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0
11 5 | 2029 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0
12 5 | 2030 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0
13 5 | 2031 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0
14 5 | 2032 | 927861 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 927861
15 | 2033 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1934140.3009 | 87682.1101 | 164818.1843
16 | 2034 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1922454.2022 | 87152.3338 | 164288.4079
17 | 2035 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1910815.768 | 86624.7182 | 163760.7924
18 | 2036 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1899220.1791 | 86099.045 | 163235.1192
19 | 2037 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1887687.1249 | 85576.2068 | 162712.2809
20 | 2038 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1876211.9613 | 85055.9929 | 162192.0671
21 | 2039 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1865064.5744 | 84550.6385 | 161686.7127
22 | 2040 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1854614.6136 | 84076.9011 | 161212.9752
23 | 2041 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1844794.9693 | 83631.7384 | 160767.8125
24 | 2042 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1835549.5746 | 83212.6086 | 160348.6828
25 | 2043 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1826789.2332 | 82815.4683 | 159951.5424
26 | 2044 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1818472.7305 | 82438.4488 | 159574.523
27 | 2045 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1810568.6378 | 82080.1255 | 159216.1997
28 | 2046 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1803054.4415 | 81739.4777 | 158875.5519
29 | 2047 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1795898.228 | 81415.0587 | 158551.1329
30 | 2048 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1789083.4855 | 81106.1199 | 158242.1941
31 | 2049 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1782570.4327 | 80810.8579 | 157946.932
32 | 2050 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1776335.9714 | 80528.2255 | 157664.2996
33 | 2051 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1770364.7965 | 80257.5289 | 157393.603
34 | 2052 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1764628.0179 | 79997.4584 | 157133.5325
35 | 2053 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1759118.7077 | 79747.6999 | 156883.774
36 | 2054 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1753817.0871 | 79507.3568 | 156643.4309
37 | 2055 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1748702.1737 | 79275.4778 | 156411.552
38 | 2056 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1743768.872 | 79051.8321 | 156187.9062
39 | 2057 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1739002.1933 | 78835.74 | 155971.8141
40 | 2058 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1734394.2851 | 78626.8455 | 155762.9197
41 | 2059 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1729937.5454 | 78424.8042 | 155560.8783
42 | 2060 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1725628.0548 | 78229.4382 | 155365.5123
43 | 2061 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1721452.6866 | 78040.1525 | 155176.2267
44 | 2062 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1717409.0838 | 77856.8402 | 154992.9144
45 | 2063 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1713489.511 | 77679.1507 | 154815.2249
46 | 2064 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1709685.0639 | 77506.6803 | 154642.7545
47 | 2065 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1705998.9972 | 77339.5766 | 154475.6507
48 | 2066 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1702409.2512 | 77176.8394 | 154312.9136
49 | 2067 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1698922.9841 | 77018.7934 | 154154.8675
50 | 2068 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1694059.4819 | 76798.3119 | 153934.386
51 | 2069 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1684880.611 | 76382.1979 | 153518.2721
52 | 2070 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1681762.9708 | 76240.8631 | 153376.9373
53 | 2071 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1678725.5038 | 76103.1629 | 153239.2371
54 | 2072 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1675770.9201 | 75969.2202 | 153105.2943
55 | 2073 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1672889.2854 | 75838.5844 | 152974.6586
56 | 2074 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1670080.3455 | 75711.2443 | 152847.3184
57 | 2075 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1667344.761 | 75587.2296 | 152723.3037
58 | 2076 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1664673.1737 | 75466.1161 | 152602.1903
59 | 2077 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1662072.456 | 75348.2154 | 152484.2896
60 | 2078 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1659539.9923 | 75233.409 | 152369.4832
61 | 2079 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1657057.4722 | 75120.8667 | 152256.9409
62 | 2080 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1654643.1597 | 75011.4165 | 152147.4907
63 | 2081 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1652285.505 | 74904.5349 | 152040.609
64 | 2082 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1649975.0386 | 74799.7924 | 151935.8666
65 | 2083 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1647726.58 | 74697.861 | 151833.9352
66 | 2084 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1645530.5442 | 74598.3062 | 151734.3803
67 | 2085 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1643382.0053 | 74500.9045 | 151636.9787
68 | 2086 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1641275.1465 | 74405.3924 | 151541.4666
69 | 2087 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1639220.5812 | 74312.251 | 151448.3252
70 | 2088 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1637214.839 | 74221.3229 | 151357.3971
71 | 2089 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1635252.5888 | 74132.3665 | 151268.4406
72 | 2090 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1633330.6782 | 74045.2388 | 151181.3129
73 | 2091 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1631451.9091 | 73960.0668 | 151096.141
74 | 2092 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1629867.9812 | 73888.2612 | 151024.3354
75 | 2093 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1628324.453 | 73818.2871 | 150954.3612
76 | 2094 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1626807.3549 | 73749.5111 | 150885.5853
77 | 2095 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1625325.8571 | 73682.3491 | 150818.4232
78 | 2096 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1623873.1179 | 73616.4907 | 150752.5649
79 | 2097 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1622447.2417 | 73551.8502 | 150687.9244
80 | 2098 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1621046.552 | 73488.3515 | 150624.4257
81 | 2099 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1619664.7166 | 73425.7075 | 150561.7817
82 | 2100 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1618303.8503 | 73364.0141 | 150500.0883
83 | 2101 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1616972.7995 | 73303.6724 | 150439.7466
84 | 2102 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1615670.4078 | 73244.6299 | 150380.7041
85 | 2103 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1614381.6681 | 73186.2064 | 150322.2805
86 | 2104 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1613111.7034 | 73128.6339 | 150264.7081
87 | 2105 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1611870.8915 | 73072.3831 | 150208.4572
88 | 2106 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1610644.8385 | 73016.8013 | 150152.8755
89 | 2107 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1609443.776 | 72962.3525 | 150098.4266
90 | 2108 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1608262.2913 | 72908.7912 | 150044.8653
91 | 2109 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1607103.1117 | 72856.2411 | 149992.3152
92 | 2110 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1605971.6093 | 72804.9456 | 149941.0198
93 | 2111 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1604861.8484 | 72754.6359 | 149890.71
94 | 2112 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1603761.6731 | 72704.7606 | 149840.8348
95 | 2113 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1602687.4501 | 72656.0619 | 149792.1361
96 | 2114 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1601625.7781 | 72607.9322 | 149744.0064
97 | 2115 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1600582.308 | 72560.6276 | 149696.7018
98 | 2116 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1599553.3549 | 72513.9812 | 149650.0553
99 | 2117 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1598543.8201 | 72468.215 | 149604.2892
100 | 2118 | 0 | 34110.5389 | 7963.6834 | 28425.4491 | 6636.4028 | Inc. in TTS Labor | 1597551.7835 | 72423.2422 | 149559.3163
Total |  | 959861 | 2933506.3456 | 684876.7697 | 2444588.6213 | 570730.6414 | 0 | 145990463.5275 | 6618316.1026 | 14211879.4806
Notes:
1 Capital pipeline costs include discharge pipeline from TTS to tributary arroyo to Mangas Wash, energy dissipation structure, and a tank.
2 Replacement O&M costs are estimated at 1.8% of the total capital cost for the complete water conveyance system. A higher percentage of capital cost is estimated given that existing pumps, pipelines, tanks and reservoirs will be utilized initially up until their associated life expectancies are met and will require replacement sooner than if new equipment was utilized initially.
3 Routine maintenance is estimated at 1.5% of the total capital cost for the complete water conveyance system. Routine maintenance includes materials needed for preventative maintenance such as mechanical seals, lubricant, valve sleeves, fuses, etc.
4 Labor for water conveyance is included in labor for the TTS. TTS Labor is provided on the TTS Cash Flow sheet.
5 The No. 3 PLS Overflow Pond will be closed at the end of Year 9 and a new 20,000 gallon plastic above ground storage tank will be installed in its place to collect low TDS and sulfate concentration waters from the 3A stockpile seepage collection and interceptor systems. There is no replacement O&M or routine maintenance applied to Years 10 through 14.
Cost estimate backup details are included in Attachment B to the Tyrone Water Treatment Cost Basis Document.
Costs do not include indirect costs
|  |  | 5456610.2295 | 613273.6262 | 6069883.8556
-2451500.7404

## TTS Cash Flow
Inputs
Date: | REV 0 July 29, 2019 | [8 empty] | New Cost | 7232445.0003
Project No.: | 18106417 | [8 empty] | Replacement O&M Percentage | 1.5%
Subject: | STS Direct Cost Cash Flow by Year in Current Cost Dollars | [8 empty] | Routine Maintenance Percentage | 1.5%
Project Short Title: | Tyrone Mine Closure Closeout Plan | [8 empty] | Avg ($/kWh) Year 1 through 14 | 0.044694
[10 empty] | Avg ($/kWh) Year 15 through 100 | 0.045334
Year | Capital | Labor | Replacement O&M | Routine Maintenance | Reagents |  |  |  | Analytical | Power | Total Annual Cost
[5 empty] | Lime (CaO) | Flocculent | Acid (35% HCl) | Membrane Chemicals
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224 | 0 | 3224
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224 | 0 | 3224
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224 | 0 | 3224
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224 | 0 | 3224
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224 | 0 | 3224
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224 | 0 | 3224
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224 | 0 | 3224
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224 | 0 | 3224
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224 | 0 | 3224
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224 | 0 | 3224
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224 | 0 | 3224
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3224 | 0 | 3224
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1612 | 0 | 1612
14 | 7232445.0003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1612 | 0 | 7234057.0003
15 | 0 | 1213843.075 | 108486.675 | 108486.675 | 1055002.1745 | 189396.7609 | 4783.1699 | 110388.2792 | 30628 | 71344.8033 | 2892359.6128
16 | 0 | 1213843.075 | 108486.675 | 108486.675 | 1043182.7888 | 187959.9622 | 4732.9574 | 109550.8533 | 30628 | 70803.5685 | 2877674.5552
17 | 0 | 1213843.075 | 108486.675 | 108486.675 | 1031477.718 | 186533.905 | 4683.1202 | 108719.6881 | 30628 | 70266.38 | 2863125.2364
18 | 0 | 1213843.075 | 108486.675 | 108486.675 | 1019883.586 | 185118.2243 | 4633.6457 | 107894.5707 | 30628 | 69733.1002 | 2848707.5519
19 | 0 | 1213843.075 | 108486.675 | 108486.675 | 1008413.7547 | 183714.5394 | 4584.5904 | 107076.4451 | 30628 | 69204.3392 | 2834438.0938
20 | 0 | 1213843.075 | 108486.675 | 108486.675 | 997067.6246 | 182322.9721 | 4535.9586 | 106265.382 | 30628 | 68680.1428 | 2820316.5051
21 | 0 | 1213843.075 | 108486.675 | 108486.675 | 986096.0168 | 180978.0204 | 4488.9559 | 105481.4884 | 30628 | 68173.5063 | 2806662.4129
22 | 0 | 1213843.075 | 108486.675 | 108486.675 | 975823.4135 | 179724.4425 | 4445.1465 | 104750.8512 | 30628 | 67701.2898 | 2793889.5685
23 | 0 | 1213843.075 | 108486.675 | 108486.675 | 966167.1687 | 178551.0994 | 4404.1411 | 104066.9783 | 30628 | 67259.2974 | 2781893.11
24 | 0 | 1213843.075 | 108486.675 | 108486.675 | 957072.1049 | 177450.8951 | 4365.6917 | 103425.7337 | 30628 | 66844.856 | 2770603.7064
25 | 0 | 1092458.7675 | 108486.675 | 108486.675 | 948446.9766 | 176411.5405 | 4329.3689 | 102819.9547 | 30628 | 66453.3364 | 2638521.2946
26 | 0 | 1092458.7675 | 108486.675 | 108486.675 | 940247.637 | 175426.9955 | 4294.9615 | 102246.1211 | 30628 | 66082.4632 | 2628358.2958
27 | 0 | 1092458.7675 | 108486.675 | 108486.675 | 932443.3937 | 174493.244 | 4262.3292 | 101701.892 | 30628 | 65730.7237 | 2618691.7002
28 | 0 | 1092458.7675 | 108486.675 | 108486.675 | 925007.6431 | 173606.6932 | 4231.3465 | 101185.1735 | 30628 | 65396.7645 | 2609487.7383
29 | 0 | 1092458.7675 | 108486.675 | 108486.675 | 917912.6354 | 172763.8303 | 4201.8905 | 100693.9181 | 30628 | 65079.2623 | 2600711.654
30 | 0 | 1092458.7675 | 108486.675 | 108486.675 | 911138.694 | 171962.0226 | 4173.8694 | 100226.5913 | 30628 | 64777.2254 | 2592338.5203
31 | 0 | 1092458.7675 | 108486.675 | 108486.675 | 904651.3693 | 171196.8227 | 4147.1275 | 99780.6011 | 30628 | 64488.9785 | 2584325.0166
32 | 0 | 1092458.7675 | 108486.675 | 108486.675 | 898427.5893 | 170465.1977 | 4121.5591 | 99354.1798 | 30628 | 64213.3791 | 2576642.0225
33 | 0 | 1092458.7675 | 108486.675 | 108486.675 | 892450.438 | 169764.8298 | 4097.083 | 98945.9764 | 18941 | 63949.554 | 2557580.9986
34 | 0 | 1092458.7675 | 108486.675 | 108486.675 | 886694.8471 | 169092.5108 | 4073.5871 | 98554.1209 | 18941 | 63696.2948 | 2550484.4782
35 | 0 | 1092458.7675 | 108486.675 | 108486.675 | 881151.995 | 168447.0951 | 4051.0314 | 98177.9459 | 18941 | 63453.17 | 2543654.3549
36 | 0 | 1092458.7675 | 108486.675 | 108486.675 | 875800.9639 | 167825.6805 | 4029.3145 | 97815.7598 | 18941 | 63219.0863 | 2537063.9225
37 | 0 | 1092458.7675 | 108486.675 | 108486.675 | 870627.0267 | 167226.5614 | 4008.3768 | 97466.5683 | 18941 | 62993.4011 | 2530695.0519
38 | 0 | 1092458.7675 | 108486.675 | 108486.675 | 865622.3502 | 166648.6199 | 3988.1792 | 97129.7201 | 18941 | 62775.6935 | 2524537.6805
39 | 0 | 1092458.7675 | 108486.675 | 108486.675 | 860774.2545 | 166090.258 | 3968.6658 | 96804.2836 | 18941 | 62565.3614 | 2518575.9408
40 | 0 | 1092458.7675 | 108486.675 | 108486.675 | 856075.4969 | 165550.5673 | 3949.805 | 96489.7296 | 18941 | 62362.0626 | 2512800.7789
41 | 0 | 1092458.7675 | 108486.675 | 108486.675 | 851517.7207 | 165028.4347 | 3931.5578 | 96185.409 | 18941 | 62165.3779 | 2507201.6176
42 | 0 | 971074.46 | 108486.675 | 108486.675 | 847095.5274 | 164523.1842 | 3913.9005 | 95890.9281 | 18941 | 61975.0526 | 2380387.4029
43 | 0 | 971074.46 | 108486.675 | 108486.675 | 842801.8326 | 164034.0096 | 3896.8051 | 95605.8169 | 18941 | 61790.783 | 2375118.0572
44 | 0 | 971074.46 | 108486.675 | 108486.675 | 838631.626 | 163560.2103 | 3880.247 | 95329.667 | 18941 | 61612.3052 | 2370002.8655
45 | 0 | 971074.46 | 108486.675 | 108486.675 | 834578.3188 | 163101.0036 | 3864.1989 | 95062.0224 | 18941 | 61439.3243 | 2365033.678
46 | 0 | 971074.46 | 108486.675 | 108486.675 | 830633.9294 | 162655.2931 | 3848.6224 | 94802.2438 | 18941 | 61271.4274 | 2360200.3261
47 | 0 | 971074.46 | 108486.675 | 108486.675 | 826798.4577 | 162223.1348 | 3833.5196 | 94550.364 | 18941 | 61108.6356 | 2355502.9217
48 | 0 | 971074.46 | 108486.675 | 108486.675 | 823055.2416 | 161802.307 | 3818.8127 | 94305.0881 | 18941 | 60950.1119 | 2350920.3713
49 | 0 | 971074.46 | 108486.675 | 108486.675 | 819408.6053 | 161393.4505 | 3804.5242 | 94066.7897 | 18941 | 60796.0977 | 2346458.2774
50 | 0 | 971074.46 | 108486.675 | 108486.675 | 814712.7391 | 160828.7001 | 3784.7875 | 93737.6297 | 18941 | 60583.3591 | 2340636.0255
51 | 0 | 971074.46 | 108486.675 | 108486.675 | 810616.5834 | 159772.4756 | 3747.8751 | 93122.0183 | 18941 | 60185.4847 | 2334433.2472
52 | 0 | 971074.46 | 108486.675 | 108486.675 | 807899.0373 | 159414.6338 | 3735.3695 | 92913.4533 | 18941 | 60050.6875 | 2331001.9914
53 | 0 | 971074.46 | 108486.675 | 108486.675 | 805249.4901 | 159065.9714 | 3723.1846 | 92710.2384 | 18941 | 59919.3481 | 2327657.0426
54 | 0 | 971074.46 | 108486.675 | 108486.675 | 802668.4488 | 158726.521 | 3711.3216 | 92512.3926 | 18941 | 59791.4788 | 2324398.9729
55 | 0 | 971074.46 | 108486.675 | 108486.675 | 800151.8109 | 158395.8411 | 3699.7652 | 92319.6587 | 18941 | 59666.9134 | 2321222.7992
56 | 0 | 971074.46 | 108486.675 | 108486.675 | 797697.02 | 158073.5154 | 3688.5007 | 92131.7939 | 18941 | 59545.4949 | 2318125.135
57 | 0 | 971074.46 | 108486.675 | 108486.675 | 795304.4155 | 157759.6591 | 3677.5322 | 91948.8655 | 18941 | 59427.2668 | 2315106.5491
58 | 0 | 971074.46 | 108486.675 | 108486.675 | 792968.6352 | 157453.478 | 3666.832 | 91770.4104 | 18941 | 59311.93 | 2312160.0956
59 | 0 | 971074.46 | 108486.675 | 108486.675 | 790688.494 | 157154.7722 | 3656.393 | 91596.3123 | 18941 | 59199.409 | 2309284.1905
60 | 0 | 971074.46 | 108486.675 | 108486.675 | 788468.0871 | 156864.1131 | 3646.2351 | 91426.9042 | 18941 | 59089.9192 | 2306484.0688
61 | 0 | 971074.46 | 108486.675 | 108486.675 | 786293.3976 | 156579.687 | 3636.2952 | 91261.1288 | 18941 | 58982.7773 | 2303742.0959
62 | 0 | 971074.46 | 108486.675 | 108486.675 | 784172.1391 | 156302.457 | 3626.6067 | 91099.5477 | 18941 | 58878.3461 | 2301067.9066
63 | 0 | 971074.46 | 108486.675 | 108486.675 | 782099.6944 | 156031.7361 | 3617.1456 | 90941.7604 | 18941 | 58776.367 | 2298455.5135
64 | 0 | 971074.46 | 108486.675 | 108486.675 | 780070.4104 | 155767.0145 | 3607.8943 | 90787.4696 | 18941 | 58676.6477 | 2295898.2466
65 | 0 | 971074.46 | 108486.675 | 108486.675 | 778090.8557 | 155508.8448 | 3598.8719 | 90636.9977 | 18941 | 58579.3965 | 2293403.7766
66 | 0 | 971074.46 | 108486.675 | 108486.675 | 776156.1751 | 155256.8425 | 3590.065 | 90490.1202 | 18941 | 58484.4685 | 2290966.4814
67 | 0 | 971074.46 | 108486.675 | 108486.675 | 774261.1932 | 155010.0869 | 3581.4416 | 90346.3009 | 18941 | 58391.5169 | 2288579.3494
68 | 0 | 971074.46 | 108486.675 | 108486.675 | 772402.2205 | 154768.2991 | 3572.9917 | 90205.3769 | 18941 | 58300.4366 | 2286238.1348
69 | 0 | 971074.46 | 108486.675 | 108486.675 | 770587.5383 | 154532.4116 | 3564.748 | 90067.8919 | 18941 | 58211.579 | 2283952.9788
70 | 0 | 971074.46 | 108486.675 | 108486.675 | 768811.212 | 154301.715 | 3556.6857 | 89933.4324 | 18941 | 58124.6767 | 2281716.5319
71 | 0 | 971074.46 | 108486.675 | 108486.675 | 767073.5275 | 154076.298 | 3548.808 | 89802.05 | 18941 | 58039.7633 | 2279529.2567
72 | 0 | 971074.46 | 108486.675 | 108486.675 | 765368.8462 | 153855.3931 | 3541.0879 | 89673.2975 | 18941 | 57956.5495 | 2277383.9842
73 | 0 | 971074.46 | 108486.675 | 108486.675 | 763705.356 | 153640.2986 | 3533.5709 | 89547.9315 | 18941 | 57875.5246 | 2275291.4916
74 | 0 | 971074.46 | 108486.675 | 108486.675 | 762162.3615 | 153459.1952 | 3527.2418 | 89442.3769 | 18941 | 57807.3038 | 2273387.2892
75 | 0 | 971074.46 | 108486.675 | 108486.675 | 760652.5056 | 153282.7718 | 3521.0762 | 89339.55 | 18941 | 57740.846 | 2271525.5596
76 | 0 | 971074.46 | 108486.675 | 108486.675 | 759163.7339 | 153109.1257 | 3515.0077 | 89238.3419 | 18941 | 57675.4344 | 2269690.4536
77 | 0 | 971074.46 | 108486.675 | 108486.675 | 757702.8441 | 152939.184 | 3509.0687 | 89139.2929 | 18941 | 57611.4182 | 2267890.6179
78 | 0 | 971074.46 | 108486.675 | 108486.675 | 756265.6663 | 152772.4124 | 3503.2404 | 89042.0915 | 18941 | 57548.5962 | 2266120.8167
79 | 0 | 971074.46 | 108486.675 | 108486.675 | 754850.2981 | 152608.5403 | 3497.5135 | 88946.58 | 18941 | 57486.8664 | 2264378.6083
80 | 0 | 971074.46 | 108486.675 | 108486.675 | 753455.5103 | 152447.4044 | 3491.8822 | 88852.6633 | 18941 | 57426.1673 | 2262662.4376
81 | 0 | 971074.46 | 108486.675 | 108486.675 | 752074.9792 | 152288.0969 | 3486.3148 | 88759.8123 | 18941 | 57366.157 | 2260964.1702
82 | 0 | 971074.46 | 108486.675 | 108486.675 | 750713.4449 | 152131.3632 | 3480.8374 | 88668.4614 | 18941 | 57307.1162 | 2259290.0332
83 | 0 | 971074.46 | 108486.675 | 108486.675 | 749374.5219 | 151977.6082 | 3475.464 | 88578.8466 | 18941 | 57249.1975 | 2257644.4482
84 | 0 | 971074.46 | 108486.675 | 108486.675 | 748059.7457 | 151827.1183 | 3470.2048 | 88491.1349 | 18941 | 57192.5087 | 2256029.5223
85 | 0 | 971074.46 | 108486.675 | 108486.675 | 746756.9817 | 151678.2117 | 3465.0008 | 88404.3459 | 18941 | 57136.4163 | 2254429.7665
86 | 0 | 971074.46 | 108486.675 | 108486.675 | 745466.3351 | 151530.7914 | 3459.8489 | 88318.4233 | 18941 | 57080.8838 | 2252845.0925
87 | 0 | 971074.46 | 108486.675 | 108486.675 | 744200.798 | 151386.7948 | 3454.8166 | 88234.4961 | 18941 | 57026.641 | 2251292.3564
88 | 0 | 971074.46 | 108486.675 | 108486.675 | 742951.3025 | 151245.0366 | 3449.8625 | 88151.8736 | 18941 | 56973.2414 | 2249760.1265
89 | 0 | 971074.46 | 108486.675 | 108486.675 | 741720.4578 | 151105.7235 | 3444.9938 | 88070.6761 | 18941 | 56920.7629 | 2248251.4241
90 | 0 | 971074.46 | 108486.675 | 108486.675 | 740506.461 | 150968.6796 | 3440.2045 | 87990.8013 | 18941 | 56869.1392 | 2246764.0955
91 | 0 | 971074.46 | 108486.675 | 108486.675 | 739309.9952 | 150833.9601 | 3435.4964 | 87912.2812 | 18941 | 56818.391 | 2245298.9339
92 | 0 | 849690.1525 | 108486.675 | 108486.675 | 738134.7022 | 150702.0555 | 3430.8866 | 87835.4017 | 18941 | 56768.7032 | 2122476.2518
93 | 0 | 849690.1525 | 108486.675 | 108486.675 | 736977.4277 | 150572.5756 | 3426.3616 | 87759.9355 | 18941 | 56719.9288 | 2121060.7317
94 | 0 | 849690.1525 | 108486.675 | 108486.675 | 735829.2885 | 150444.3114 | 3421.8791 | 87685.1777 | 18941 | 56671.6123 | 2119656.7714
95 | 0 | 849690.1525 | 108486.675 | 108486.675 | 734702.9831 | 150319.0197 | 3417.5005 | 87612.1526 | 18941 | 56624.4156 | 2118280.574
96 | 0 | 849690.1525 | 108486.675 | 108486.675 | 733584.6535 | 150194.6874 | 3413.1554 | 87539.6865 | 18941 | 56577.5802 | 2116914.2655
97 | 0 | 849690.1525 | 108486.675 | 108486.675 | 732482.7745 | 150072.6065 | 3408.889 | 87468.5327 | 18941 | 56531.5929 | 2115568.898
98 | 0 | 849690.1525 | 108486.675 | 108486.675 | 731394.1742 | 149952.3313 | 3404.6856 | 87398.4314 | 18941 | 56486.2859 | 2114240.4108
99 | 0 | 849690.1525 | 108486.675 | 108486.675 | 730319.6211 | 149833.883 | 3400.5462 | 87329.3948 | 18941 | 56441.667 | 2112929.6145
100 | 0 | 849690.1525 | 108486.675 | 108486.675 | 729262.7728 | 149717.9184 | 3396.4935 | 87261.8058 | 18941 | 56397.9837 | 2111641.4767
Total | 7232445.0003 | 86911164.17 | 9329854.0503 | 9329854.0503 | 70905774.5885 | 13875586.4903 | 327040.5424 | 8087266.686 | 1881204 | 5226863.3534 | 213107052.9316
1 Replacement O&M and routine maintenance are estimated as a percentage of total direct capital cost. Capital replacement includes cell closure costs.
Costs do not include indirect costs
Cost estimate backup details are included in Attachment B to the Tyrone Water Treatment Cost Basis Document.

## Sludge Disposal Cash Flow 2019
Inputs
[6 empty] | New Cost | 142304.818
Date: |  | REV 0 July 29, 2019 |  |  |  | Replacement O&M | 1.5%
Project No.: |  | 18106417 |  |  |  | Sludge disposal ($/cy) | 3.0327
Subject: |  | Sludge Disposal Direct Cost Cash Flow by Year in Current Cost Dollars
Project Short Title: |  | Tyrone Mine Closure Closeout Plan
Year Following Closure | Year | Capital | Replacement O&M1 | Routine Maintenance2 | O&M Labor2 | Annual Sludge Production/ Removal (cy/yr) | Total Operating Cost
1 | 2019 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2020 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2021 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2022 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2023 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2024 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2025 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2026 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2027 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2028 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2029 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2030 | 0 | 0 | 0 | 0 | 0 | 0
13 | 2031 | 0 | 0 | 0 | 0 | 0 | 0
14 | 2032 | 142304.818 | 0 | 0 | 0 | 0 | 142304.818
15 | 2033 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 24328.666 | 75915.8104
16 | 2034 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 24056.1074 | 75089.2255
17 | 2035 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 23786.185 | 74270.6351
18 | 2036 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 23518.8208 | 73459.8032
19 | 2037 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 23254.3231 | 72657.6643
20 | 2038 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 22992.6779 | 71864.1763
21 | 2039 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 22739.6694 | 71096.8804
22 | 2040 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 22502.7801 | 70378.4692
23 | 2041 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 22280.1042 | 69703.1628
24 | 2042 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 22070.3693 | 69067.1025
25 | 2043 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 21871.4712 | 68463.9069
26 | 2044 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 21682.392 | 67890.4887
27 | 2045 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 21502.4238 | 67344.7015
28 | 2046 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 21330.9532 | 66824.6846
29 | 2047 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 21167.3402 | 66328.4976
30 | 2048 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 21011.1311 | 65854.7641
31 | 2049 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 20861.5314 | 65401.0752
32 | 2050 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 20718.0092 | 64965.8171
33 | 2051 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 20580.1743 | 64547.807
34 | 2052 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 20447.4486 | 64145.2916
35 | 2053 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 20319.6288 | 63757.654
36 | 2054 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 20196.2324 | 63383.4313
37 | 2055 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 20076.9199 | 63021.5937
38 | 2056 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 19961.5106 | 62671.5933
39 | 2057 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 19849.712 | 62332.5432
40 | 2058 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 19741.3573 | 62003.9371
41 | 2059 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 19636.2536 | 61685.1905
42 | 2060 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 19534.2765 | 61375.9259
43 | 2061 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 19435.2626 | 61075.6477
44 | 2062 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 19339.0964 | 60784.0056
45 | 2063 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 19245.6259 | 60500.5389
46 | 2064 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 19154.6671 | 60224.6893
47 | 2065 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 19066.22 | 59956.4568
48 | 2066 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 18979.9003 | 59694.6762
49 | 2067 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 18895.8078 | 59439.6499
50 | 2068 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 18787.5197 | 59111.246
51 | 2069 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 18693.0611 | 58824.7826
52 | 2070 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 18630.3937 | 58634.7319
53 | 2071 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 18569.2943 | 58449.4367
54 | 2072 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 18509.7747 | 58268.9324
55 | 2073 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 18451.7403 | 58092.9321
56 | 2074 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 18395.1321 | 57921.2571
57 | 2075 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 18339.9579 | 57753.9311
58 | 2076 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 18286.0941 | 57590.579
59 | 2077 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 18233.5134 | 57431.1181
60 | 2078 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 18182.3101 | 57275.8347
61 | 2079 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 18132.1612 | 57123.7484
62 | 2080 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 18083.2443 | 56975.3989
63 | 2081 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 18035.4531 | 56830.4632
64 | 2082 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17988.6572 | 56688.5458
65 | 2083 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17943.0081 | 56550.1063
66 | 2084 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17898.3938 | 56414.805
67 | 2085 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17854.6949 | 56282.2801
68 | 2086 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17811.8265 | 56152.2734
69 | 2087 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17769.9793 | 56025.3642
70 | 2088 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17729.0167 | 55901.1374
71 | 2089 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17688.9452 | 55779.613
72 | 2090 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17649.6347 | 55660.3967
73 | 2091 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17611.2742 | 55544.061
74 | 2092 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17575.6922 | 55436.1522
75 | 2093 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17540.8745 | 55330.5609
76 | 2094 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17506.543 | 55226.4441
77 | 2095 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17472.8544 | 55124.2773
78 | 2096 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17439.7127 | 55023.7687
79 | 2097 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17407.0739 | 54924.7854
80 | 2098 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17374.9096 | 54827.2413
81 | 2099 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17343.0742 | 54730.6943
82 | 2100 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17311.6768 | 54635.4759
83 | 2101 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17280.8008 | 54541.8387
84 | 2102 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17250.4817 | 54449.8903
85 | 2103 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17220.4396 | 54358.7819
86 | 2104 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17190.6769 | 54268.5209
87 | 2105 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17161.4932 | 54180.016
88 | 2106 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17132.6795 | 54092.6329
89 | 2107 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17104.2958 | 54006.5542
90 | 2108 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17076.3007 | 53921.6537
91 | 2109 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17048.7098 | 53837.9793
92 | 2110 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 17021.6072 | 53755.7856
93 | 2111 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 16994.9201 | 53674.8519
94 | 2112 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 16968.4437 | 53594.5572
95 | 2113 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 16942.4708 | 53515.7894
96 | 2114 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 16916.6817 | 53437.5794
97 | 2115 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 16891.2721 | 53360.5198
98 | 2116 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 16866.1686 | 53284.3889
99 | 2117 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 16841.3891 | 53209.2404
100 | 2118 | 0 | 2134.5723 | Included in Total Operating Cost | Included in Total Operating Cost | 16817.0179 | 53135.33
Total |  | 142304.818 | 183573.2153 | 0 | 0 | 1635108.3904 | 5284650.6015
Notes:
1 Capital replacement is estimated at 1.5% of the total capital cost and includes estimated costs associated with closure of each of the four individual cells comprising the sludge disposal facility (approximately 408,777 cubic yards per cell). Closure includes grading, three foot of earthen cover, and revegetation costs. Initial capital cost for construction of sludge disposal facility (by RS Means) shown in Year 14.
2 Routine Maintenance and Operation and Maintanance Labor is included in the Total Operating Cost calculation. Costs based on 2019 RS Means estimate of $3.03 per/cy for loading, hauling, and placing of sludge at the sludge disposal facility.
Cost estimate backup details are included in Attachment B to the Tyrone Water Treatment Cost Basis Document.
Costs do not include indirect costs
185746

## TTS Capital Cost
Date: |  | REV 0 July 29, 2019
Project No.: |  | 18106417
Subject: |  | STS Capital Cost Estimate Details
Project Short Title: |  | Tyrone Mine Closure Closeout Plan
Item |  | Description |  |  | Qty | UOM | Unit $ | Extended
Equipment Cost
Membrane System, UF and RO systems | a | 1,600 gpm, UF is 2 50% units and RO is 3 33% units for flexibility |  |  | 1 | each | 1345700 | 1345700
Reaction Tank | a | Four 32,000 gallon tanks for flexibility, appx 120 min reaction time, baffles, ladder, platform, mixer mount and mixer |  |  | 4 | each | 129000 | 516000
Floc Tank | a | 7,000 gallon tank and mixer |  |  | 1 | each | 26000 | 26000
Sludge Densification Tank | a | 2 tanks at 450 gal, with internal baffles, mixer mount and mixer, legs for gravity overflow to reaction tank |  |  | 2 | each | 88400 | 176800
Thickener/Clarifier | a | 80' diameter, with feedwell, bridge, ladder, platform |  |  | 1 | each | 377200 | 377200
Sludge Pump | a | 29 gpm |  |  | 2 | each | 15000 | 30000
Underflow Pump | a | 3 Recycles 152 gpm |  |  | 2 | each | 20000 | 40000
Polymer system | a | 10 mg/L - 0.97 gph |  |  | 1 | each | 18525 | 18525
Lime Silo and Slaker System | a | 36,780 lb/day - 39 gpm, 10% slurry |  |  | 1 | each | 985000 | 985000
pH control system (acid addition) | a | 6.65 mg/L - 1.07 gph, 0.35 concentration |  |  | 2 | each | 7053 | 14106
Effluent Neutralization Tank | a | 32,000 gallon tank with mixer |  |  | 1 | each | 129000 | 129000
Sludge Holding Tank | a | 13,000 gal |  |  | 1 | each | 33000 | 33000
Filter Press System | a | 3 - 100 ft3 including platform and conveyor |  |  | 3 | each | 352667 | 1058001
Filtrate Tank | a | 3,000 gal |  |  | 1 | each | 10000 | 10000
Filtrate Pump | a | 9 gpm |  |  | 2 | each | 6700 | 13400
Process Water Tank | a | 3,000 gal |  |  | 1 | each | 10000 | 10000
Process Water Return Pump | a | 27.97 gpm |  |  | 2 | each | 5395.9493 | 10791.8987
Air Compressor | b | For diaphragm pumps, includes air receiver |  |  | 2 | each | 15000 | 30000
Electrical Equipment | b |  |  |  | 1 | ls | 100000 | 100000
Valves and Piping | b |  |  |  | 1 | ls | 156000 | 156000
Instrumentation | b |  |  |  | 1 | ls | 50000 | 50000
Control System | b |  |  |  | 1 | ls | 50000 | 50000
Freight | b |  |  |  | 1 | ls | 100000 | 100000
Total Direct Equipment | [7 empty] | 5279523.8987
Installation Cost
Equipment Placement |  | Materials/equipment |  |  | 1 | ls | 50000 | 50000
| c | Crew size | 6 | men
| c | Duration | 35 | days
|  | Labor subtotal (Group II Laborers) |  |  | 1680 | hrs | 23.84 | 40051.2
Tank Erection (Clarifier Tank) |  | Materials/equipment |  |  | 1 | ls | 75000 | 75000
| c | Crew size | 8 | men
| c | Duration | 28 | days
|  | Ironworker |  |  | 1792 | hrs | 48.66 | 87198.72
Process Mechanical |  | Materials/equipment |  |  | 1 | ls | 30000 | 30000
| c | Crew size | 6 | men
| c | Duration | 32 | days
|  | Labor subtotal (Plumber/Pipefitter) |  |  | 1536 | hrs | 45.45 | 69811.2
Process Electrical |  | Materials/equipment |  |  | 1 | ls | 200000 | 200000
| c | Crew size | 4 | men
| c | Duration | 45 | days
|  | Labor subtotal [Electrician (Lineman/Tech)] |  |  | 1440 | hrs | 54.054 | 77837.76
Process Controls |  | Materials/equipment |  |  | 1 | ls | 5000 | 5000
| c | Crew size | 4 | men
| c | Duration | 20 | days
|  | Labor subtotal [Electrician (Lineman/Tech)] |  |  | 640 | hrs | 54.054 | 34594.56
Per Diem (Facility Electrical, Plumber) | c | Per Day |  |  | 252 | days | 50 | 12600
Structural Steel | b |  |  |  | 1 | ls | 50000 | 50000
Total Installation Cost | [7 empty] | 732093.44
Facility Cost
Site Work | b | 2 x pad area | 20800 | ft2 | 0.4775 | acre | 100000 | 47750.2296
Foundations | b | Pad area | 10400 | ft2
|  | Average thickness | 1 | ft
|  | Foundation wall width | 1 | ft
|  | Foundation wall depth | 3 | ft
|  | Footer width | 3 | ft
|  | Footer depth | 1 | ft
|  | Additional allowance | 10 | %
|  | Total concrete |  |  | 486.0251 | cy | 600 | 291615.032
Building Envelope | b | Building area | 5000 | ft2 | 5000 | ft2 | 100 | 500000
Building Electrical | b | Materials/equipment |  |  | 1 | ls | 40000 | 40000
| c | Crew size | 4 | men
| c | Duration | 15 | days
Electrical Lineman (outside) |  | Labor subtotal |  |  | 480 | hrs | 55.13 | 26462.4 | note: existing electrical will be accessible
Building Plumbing | b |  |  |  | 1 | ls | 75000 | 75000
Building HVAC | b |  |  |  | 1 | ls | 115000 | 115000
Freight (building) | d |  |  |  | 1 | ls | 25000 | 25000
Commissioning | b |  |  |  | 1 | ls | 100000 | 100000
Total Facility Cost | [7 empty] | 1220827.6616
Total Capital Cost
Total Direct Cost | [7 empty] | 7232445.0003
Indirect Costs |  |  |  |  | 22.5 | % | 7232445.0003 | 1627300.1251
Total Capital Cost | [7 empty] | 8859745.1253
Notes:
a = Cost based on quote from vendor.
b = Cost based on experience with detailed design and construction of similar treatment systems.
c = Hours based on experience with detailed design and construction of similar treatment systems, labor rates based on 2019 New Mexico rates. Per diem based on 2019 New Mexico Subsisistence, Zone and Incentive Pay Rates (per diem applies Plumber/Pipefitter and Electrical Lineman (outside) only.
d = Lump sum costs for freight have been included for the major process equipment and the building. Freight on materials is not included.
Costs do not include indirect costs

## TTS Equipment List Input
Date: | REV 0 July 29, 2019
Project No.: | 18106417
Subject: | STS Equipment List
Project Short Title: | Tyrone Mine Closure Closeout Plan
[12 empty] | 2019-03-01 | 2019
[12 empty] | Inflation | 2.43%
Equipment Name | Description | Power, hp | Footprint | Quantity | Cost | Manufacturer/Vendor/ Quote Tab Number | Base Year | Size Costed | Base Cost | Size Needed | Unit | New Cost / Base Year | # Years | Unit Cost | Notes
Spray evaporators | Including disconnects | 216 |  | 8 | 0 | SMI quote from Amulsar` - yellow highlighted rows are in process by other groups | 2012 | 45 | 32650 | 45 | gpm | 32650 | 7 | 40155.3817
Weather control and automation package |  | 2 |  | 1 | 0 | SMI quote from Amulsar` | 2012 | 45 | 27500 | 45 | gpm | 27500 | 7 | 33821.5313
SDF |  |  |  | 1 | 0 | Scaled from previous CCP | 2007 | 4013117 | 1524000 | 0 | tons | 0 | 12 | 0
Water conveyance |  |  |  | 1 | 846707.4933 | Scaled from previous CCP | 2007 | 6391 | 1388217 | 1900 | gpm | 593863.6002 | 12 | 846707.4933
Membrane System, UF and RO systems | 1,600 gpm, UF is 2 50% units and RO is 3 33% units for flexibility | 250 | 784 | 1 | 1345700 | WesTech Quote 2019 (Tab 1) | 2019 | 1600 | 1345700 | 1600 | gpm | 1345700 | 0 | 1345700
Reaction Tank | Four 32,000 gallon tanks for flexibility, appx 120 min reaction time, baffles, ladder, platform, mixer mount and mixer | NA | 1256.6371 | 4 | 516000 | WesTech Quote 2019 (Tab 1) | 2019 | 32000 | 129000 | 32000 | gal | 129000 | 0 | 129000 | Quote is for 1 - 32,000 gallon tanks, need 4 for a total reaction time of 120 min
Floc Tank | 7,000 gallon tank and mixer | 2 | 78.5398 | 1 | 26000 | Tank Equipment 2019 (Tab 2) | 2019 | 7000 | 26000 | 7000 | gal | 26000 | 0 | 26000
Sludge Densification Tank | 2 tanks at 450 gal, with internal baffles, mixer mount and mixer, legs for gravity overflow to reaction tank | 1 | 56.5487 | 2 | 176800 | WesTech Quote 2019 (Tab 1) | 2019 | 450 | 88400 | 450 | gal | 88400 | 0 | 88400
Thickener/Clarifier | 80' diameter, with feedwell, bridge, ladder, platform | 2 | 5541.7694 | 1 | 377200 | WesTech Quote 2019 (Tab 1) | 2019 | 80 | 377200 | 80 | ft | 377200 | 0 | 377200
Sludge Pump | 29 gpm | 1.5 | 16 | 2 | 30000 | Denver Industrial Pumps 2019 (Tab 3) | 2019 | 29 | 15000 | 29 | gpm | 15000 | 0 | 15000
Underflow Pump | 3 Recycles 152 gpm | 3 | 16 | 2 | 40000 | Denver Industrial Pumps 2019 (Tab 3) | 2019 | 152 | 20000 | 152 | gpm | 20000 | 0 | 20000
Polymer system | 10 mg/L - 0.97 gph | 0.3 | 16 | 1 | 18525 | Velodyne 2019 Quote (Tab 4) | 2019 | 1 | 18525 | 1 | gpm | 18525 | 0 | 18525
Lime Silo and Slaker System | 36,780 lb/day - 39 gpm, 10% slurry | 10 | 113.0973 | 1 | 985000 | Louisville Dryer Company Quote 2019 (Tab 5) | 2019 | 39 | 985000 | 39 | gpm | 985000 | 0 | 985000
pH control system (acid addition) | 6.65 mg/L - 1.07 gph, 0.35 concentration | 0.3 | 12 | 2 | 14106 | Denver Industrial Pumps 2019 (Tab 6) | 2019 | 1 | 7053 | 1 | gph | 7053 | 0 | 7053
Effluent Neutralization Tank | 32,000 gallon tank with mixer | 7.5 | 153.938 | 1 | 129000 | WesTech Quote 2019 (Tab 1) | 2019 | 32000 | 129000 | 32000 | gal | 129000 | 0 | 129000
Sludge Holding Tank | 13,000 gal | NA | 113.0973 | 1 | 33000 | Tank Equipment 2019 (Tab 2) | 2019 | 9000 | 33000 | 9000 | gal | 33000 | 0 | 33000
Filter Press System | 3 - 100 ft3 including platform and conveyor | 15 | 476 | 3 | 1058001 | WesTech Quote 2019 (Tab 1) | 2019 | 200 | 352667 | 200 | ft3 | 352667 | 0 | 352667 | Need 3 for max, 2 for avg conditions
Filtrate Tank | 3,000 gal | NA | 50.2655 | 1 | 10000 | Tank Equipment 2019 (Tab 2) | 2019 | 3000 | 10000 | 3000 | gal | 10000 | 0 | 10000
Filtrate Pump | 9 gpm | 0.5 | 16 | 2 | 13400 | Denver Industrial Pumps 2019 (Tab 3) | 2019 | 9 | 6700 | 9 | gpm | 6700 | 0 | 6700
Process Water Tank | 3,000 gal | NA | 50.2655 | 1 | 10000 | Tank Equipment 2019 (Tab 2) | 2019 | 3000 | 10000 | 3000 | gal | 10000 | 0 | 10000
Process Water Return Pump | 27.97 gpm | 1 | 16 | 2 | 10791.8987 | Denver Industrial Pumps 2019 (Tab 3) | 2019 | 28 | 5400 | 27.97 | gpm | 5395.9493 | 0 | 5395.9493
Air Compressor | For diaphragm pumps, includes air receiver | 15 | 16 | 2 | 30000 | Estimation based on previous experience | NA | NA | NA | NA | NA | NA | NA | 15000
Electrical Equipment |  | NA | NA | 1 | 100000 | Estimation based on previous experience | NA | NA | NA | NA | NA | NA | NA | 300000
Valves and Piping |  | NA | NA | 1 | 156000 | Estimation based on previous experience | NA | NA | NA | NA | NA | NA | NA | 160000
Instrumentation |  | NA | NA | 1 | 50000 | Estimation based on previous experience | NA | NA | NA | NA | NA | NA | NA | 75000
Control System |  | 5 | NA | 1 | 50000 | Estimation based on previous experience | NA | NA | NA | NA | NA | NA | NA | 200000
Freight |  | NA | NA | 1 | 100000 | Estimation based on previous experience | NA | NA | NA | NA | NA | NA | NA | 100000
Total Process Equip |  | 400 | 3240.3892 | 1 | 5279523.8987
TTS Total |  | 298.28 | 8782.1587 | Total area including the thickner which is located outside of the TTS building.
Assume building load allowance is covered under safety factor of max hp listed for equipment
NOTE - Quotes are available in referenced lettered tabs (Column F) in a separate PDF.

## TTS Calculation Summary
Date: | REV 0 July 29, 2019
Project No.: | 18106417
Subject: | Yearly Summary for TTS
Project Short Title: | Tyrone Mine Closure Closeout Plan
Year | TTS Flow Balance | [10 empty] | TTS Sulfate Concentration Balance | [6 empty] | TTS Sludge | [15 empty] | TTS Power Calculations
| MA +Interceptor Flow to HDS, gpm | MA Flow, gpm | HDS Feed (Brine Recycle, MA, Sludge Recycle), gpm | Sludge Recycle, gpm | HDS to RO, gpm | HDS to RO Bypass, gpm | RO Membrane (HDS -Bypass) Feed Flow, gpm | Permeate, gpm | Brine Flow, gpm | Brine Recycle Flow (for calculation), gpm | Effluent (Perm + RO Bypass) Flow, gpm | MA + Interceptor Sulfate, mg/L | GW Sulfate, mg/L | HDS Feed Sulfate, mg/L | HDS Effluent Sulfate AVG, mg/L | Membrane Feed Sulfate MAX, mg/L | Brine Sulfate, mg/L | Effluent Sulfate, mg/L | Sludge Dry Solids, lb/day | Sludge Dry Solids (for calculation), lb/day | Final Sludge @ 50% Moisture, lb/day | Final Sludge @ 50% Moisture, cy/year | Lime (CaO) Consumption, lb/day | Lime (CaO) Consumption, ton/year | Flocculent (Anionic Polymer) Consumption, lb/day | Flocculent (Anionic Polymer) Consumption, ton/year | Acid (35% HCl) Consumption, lb/day | Acid (35%HCl) Consumption, ton/year | Antiscalant, lb/year | Biocide, lb/year | MF High pH Cleaning Chem, lb/year | MF Low pH Cleaning Chem, lb/year | RO High pH Cleaning Chem, lb/year | RO Low pH Cleaning Chem, lb/year | Membrane Power (kwh/yr) | HDS Power (kwh/yr) | Total Power (kwh/year) | Sludge, 50% tons/year
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 1189.094 | 889.094 | 1285.2425 | 96.1485 | 925.3746 | 359.8679 | 925.3746 | 721.7922 | 203.5824 | 0 | 1081.6601 | 2811.4486 | 479 | 2788.1493 | 1600 | 2500 | 7272.7273 | 545.6654 | 89982.7373 | 114508.2963 | 179965.4745 | 24328.666 | 22581.3822 | 4121.1022 | 154.4331 | 28.184 | 62.4027 | 11.3885 | 12175.5061 | 4058.502 | 4228.2501 | 4228.2501 | 704.7083 | 704.7083 | 1220595.534 | 353167.4509 | 1573762.9849 | 32843.6991
16 | 1180.2107 | 880.2107 | 1275.4924 | 95.2817 | 918.3545 | 357.1379 | 918.3545 | 716.3165 | 202.038 | 0 | 1073.4544 | 2800.4301 | 479 | 2777.9874 | 1600 | 2500 | 7272.7273 | 545.6654 | 88974.6439 | 113475.9275 | 177949.2878 | 24056.1074 | 22328.3987 | 4074.9328 | 153.2615 | 27.9702 | 61.7476 | 11.2689 | 12083.1404 | 4027.7135 | 4196.1738 | 4196.1738 | 699.3623 | 699.3623 | 1211335.8713 | 350488.2575 | 1561824.1288 | 32475.745
17 | 1171.3921 | 871.3921 | 1265.8152 | 94.4231 | 911.387 | 354.4283 | 911.387 | 710.8818 | 200.5051 | 0 | 1065.3101 | 2789.4044 | 479 | 2767.8164 | 1600 | 2500 | 7272.7273 | 545.6654 | 87976.3007 | 112453.3345 | 175952.6013 | 23786.185 | 22077.8621 | 4029.2098 | 152.0987 | 27.758 | 61.0975 | 11.1503 | 11991.4653 | 3997.1551 | 4164.3373 | 4164.3373 | 694.0562 | 694.0562 | 1202145.4344 | 347829.0939 | 1549974.5283 | 32111.3497
18 | 1162.636 | 862.636 | 1256.2084 | 93.5724 | 904.4701 | 351.7384 | 904.4701 | 705.4867 | 198.9834 | 0 | 1057.225 | 2778.3692 | 479 | 2757.6341 | 1600 | 2500 | 7272.7273 | 545.6654 | 86987.4195 | 111440.2285 | 173974.8391 | 23518.8208 | 21829.7 | 3983.9203 | 150.9444 | 27.5474 | 60.452 | 11.0325 | 11900.4573 | 3966.8191 | 4132.7325 | 4132.7325 | 688.7887 | 688.7887 | 1193021.8697 | 345189.2792 | 1538211.1489 | 31750.4081
19 | 1153.9524 | 853.9524 | 1246.6831 | 92.7307 | 897.6118 | 349.0713 | 897.6118 | 700.1372 | 197.4746 | 0 | 1049.2085 | 2767.3393 | 479 | 2747.4541 | 1600 | 2500 | 7272.7273 | 545.6654 | 86009.1402 | 110437.7532 | 172018.2804 | 23254.3231 | 21584.1985 | 3939.1162 | 149.7999 | 27.3385 | 59.812 | 10.9157 | 11810.2204 | 3936.7401 | 4101.3955 | 4101.3955 | 683.5659 | 683.5659 | 1183975.6143 | 342571.8331 | 1526547.4475 | 31393.3362
20 | 1145.3421 | 845.3421 | 1237.2399 | 91.8978 | 890.8127 | 346.4272 | 890.8127 | 694.8339 | 195.9788 | 0 | 1041.2611 | 2756.3131 | 479 | 2737.275 | 1600 | 2500 | 7272.7273 | 545.6654 | 85041.4115 | 109445.858 | 170082.8231 | 22992.6779 | 21341.3447 | 3894.7954 | 148.6652 | 27.1314 | 59.1775 | 10.7999 | 11720.7625 | 3906.9208 | 4070.329 | 4070.329 | 678.3882 | 678.3882 | 1175007.4524 | 339976.9827 | 1514984.435 | 31040.1152
21 | 1137.0212 | 837.0212 | 1228.1131 | 91.0919 | 884.2414 | 343.8717 | 884.2414 | 689.7083 | 194.5331 | 0 | 1033.58 | 2745.4807 | 479 | 2727.2728 | 1600 | 2500 | 7272.7273 | 545.6654 | 84105.6265 | 108486.0218 | 168211.2529 | 22739.6694 | 21106.5072 | 3851.9376 | 147.5685 | 26.9313 | 58.5643 | 10.688 | 11634.3013 | 3878.1004 | 4040.3031 | 4040.3031 | 673.3839 | 673.3839 | 1166339.7115 | 337469.0561 | 1503808.7677 | 30698.5537
22 | 1129.2702 | 829.2702 | 1219.6063 | 90.3362 | 878.1166 | 341.4898 | 878.1166 | 684.9309 | 193.1856 | 0 | 1026.4207 | 2735.1 | 479 | 2717.6862 | 1600 | 2500 | 7272.7273 | 545.6654 | 83229.4605 | 107586.0322 | 166458.921 | 22502.7801 | 20886.6313 | 3811.8102 | 146.5463 | 26.7447 | 57.9928 | 10.5837 | 11553.7142 | 3851.2381 | 4012.3172 | 4012.3172 | 668.7195 | 668.7195 | 1158260.8423 | 335131.5138 | 1493392.3561 | 30378.7531
23 | 1122.0193 | 822.0193 | 1211.6441 | 89.6248 | 872.3837 | 339.2603 | 872.3837 | 680.4593 | 191.9244 | 0 | 1019.7196 | 2725.1285 | 479 | 2708.4758 | 1600 | 2500 | 7272.7273 | 545.6654 | 82405.8647 | 106738.8123 | 164811.7295 | 22280.1042 | 20679.948 | 3774.0905 | 145.5896 | 26.5701 | 57.4578 | 10.4861 | 11478.285 | 3826.095 | 3986.1225 | 3986.1225 | 664.3538 | 664.3538 | 1150699.059 | 332943.5854 | 1483642.6444 | 30078.1406
24 | 1115.2244 | 815.2244 | 1204.1781 | 88.9537 | 867.0082 | 337.1699 | 867.0082 | 676.2664 | 190.7418 | 0 | 1013.4363 | 2715.5359 | 479 | 2699.614 | 1600 | 2500 | 7272.7273 | 545.6654 | 81630.1329 | 105939.6384 | 163260.2659 | 22070.3693 | 20485.2762 | 3738.5629 | 144.6925 | 26.4064 | 56.9562 | 10.3945 | 11407.5575 | 3802.5192 | 3961.5607 | 3961.5607 | 660.2601 | 660.2601 | 1143608.6292 | 330892.0384 | 1474500.6676 | 29794.9985
25 | 1108.8086 | 808.8086 | 1197.1251 | 88.3165 | 861.93 | 335.195 | 861.93 | 672.3054 | 189.6246 | 0 | 1007.5004 | 2706.2638 | 479 | 2691.047 | 1600 | 2500 | 7272.7273 | 545.6654 | 80894.4826 | 105180.6973 | 161788.9653 | 21871.4712 | 20300.663 | 3704.871 | 143.845 | 26.2517 | 56.4823 | 10.308 | 11340.7419 | 3780.2473 | 3938.3573 | 3938.3573 | 656.3929 | 656.3929 | 1136910.3539 | 328953.9576 | 1465864.3116 | 29526.4862
26 | 1102.7341 | 802.7341 | 1190.444 | 87.7098 | 857.1196 | 333.3243 | 857.1196 | 668.5533 | 188.5663 | 0 | 1001.8776 | 2697.2912 | 479 | 2682.7552 | 1600 | 2500 | 7272.7273 | 545.6654 | 80195.1485 | 104458.2087 | 160390.2971 | 21682.392 | 20125.1635 | 3672.8423 | 143.0422 | 26.1052 | 56.0334 | 10.2261 | 11277.4497 | 3759.1499 | 3916.3775 | 3916.3775 | 652.7296 | 652.7296 | 1130565.3073 | 327118.0801 | 1457683.3874 | 29271.2292
27 | 1096.9759 | 796.9759 | 1184.1075 | 87.1316 | 852.5574 | 331.5501 | 852.5574 | 664.9948 | 187.5626 | 0 | 996.5449 | 2688.6028 | 479 | 2674.7246 | 1600 | 2500 | 7272.7273 | 545.6654 | 79529.5128 | 103769.5447 | 159059.0255 | 21502.4238 | 19958.1206 | 3642.357 | 142.2809 | 25.9663 | 55.6077 | 10.1484 | 11217.4228 | 3739.1409 | 3895.5316 | 3895.5316 | 649.2553 | 649.2553 | 1124547.6074 | 325376.9171 | 1449924.5245 | 29028.2722
28 | 1091.5116 | 791.5116 | 1178.0914 | 86.5798 | 848.2258 | 329.8656 | 848.2258 | 661.6161 | 186.6097 | 0 | 991.4817 | 2680.1873 | 479 | 2666.9451 | 1600 | 2500 | 7272.7273 | 545.6654 | 78895.3063 | 103112.4274 | 157790.6126 | 21330.9532 | 19798.965 | 3613.3111 | 141.558 | 25.8343 | 55.2035 | 10.0746 | 11160.4303 | 3720.1434 | 3875.7395 | 3875.7395 | 645.9566 | 645.9566 | 1118834.0992 | 323723.7691 | 1442557.8683 | 28796.7868
29 | 1086.3192 | 786.3192 | 1172.3718 | 86.0526 | 844.1077 | 328.2641 | 844.1077 | 658.404 | 185.7037 | 0 | 986.6681 | 2672.0273 | 479 | 2659.4004 | 1600 | 2500 | 7272.7273 | 545.6654 | 78290.1623 | 102484.4813 | 156580.3246 | 21167.3402 | 19647.1026 | 3585.5962 | 140.8707 | 25.7089 | 54.8192 | 10.0045 | 11106.2462 | 3702.0821 | 3856.9228 | 3856.9228 | 642.8205 | 642.8205 | 1113402.1439 | 322152.0856 | 1435554.2295 | 28575.9092
30 | 1081.3823 | 781.3823 | 1166.9307 | 85.5484 | 840.1901 | 326.7406 | 840.1901 | 655.3483 | 184.8418 | 0 | 982.0889 | 2664.1146 | 479 | 2652.0833 | 1600 | 2500 | 7272.7273 | 545.6654 | 77712.4026 | 101884.0215 | 155424.8052 | 21011.1311 | 19502.1125 | 3559.1355 | 140.2169 | 25.5896 | 54.4536 | 9.9378 | 11054.7015 | 3684.9005 | 3839.0225 | 3839.0225 | 639.8371 | 639.8371 | 1108234.7757 | 320656.9578 | 1428891.7335 | 28365.0269
31 | 1076.6733 | 776.6733 | 1161.7381 | 85.0648 | 836.4514 | 325.2867 | 836.4514 | 652.4321 | 184.0193 | 0 | 977.7188 | 2656.4237 | 479 | 2644.97 | 1600 | 2500 | 7272.7273 | 545.6654 | 77159.0888 | 101308.0986 | 154318.1776 | 20861.5314 | 19363.257 | 3533.7944 | 139.593 | 25.4757 | 54.1047 | 9.8741 | 11005.51 | 3668.5033 | 3821.9396 | 3821.9396 | 636.9899 | 636.9899 | 1103303.3309 | 319230.0922 | 1422533.4231 | 28163.0674
32 | 1072.1731 | 772.1731 | 1156.7733 | 84.6002 | 832.8768 | 323.8965 | 832.8768 | 649.6439 | 183.2329 | 0 | 973.5404 | 2648.9399 | 479 | 2638.0472 | 1600 | 2500 | 7272.7273 | 545.6654 | 76628.2532 | 100754.7373 | 153256.5063 | 20718.0092 | 19230.0426 | 3509.4828 | 138.9964 | 25.3668 | 53.7712 | 9.8132 | 10958.477 | 3652.8257 | 3805.6062 | 3805.6062 | 634.2677 | 634.2677 | 1098588.2654 | 317865.8339 | 1416454.0992 | 27969.3124
33 | 1067.8674 | 767.8674 | 1152.0206 | 84.1533 | 829.4548 | 322.5658 | 829.4548 | 646.9748 | 182.4801 | 0 | 969.5405 | 2641.6551 | 479 | 2631.3075 | 1600 | 2500 | 7272.7273 | 545.6654 | 76118.4528 | 100222.489 | 152236.9057 | 20580.1743 | 19102.107 | 3486.1345 | 138.4253 | 25.2626 | 53.4518 | 9.755 | 10913.4533 | 3637.8178 | 3789.9706 | 3789.9706 | 631.6618 | 631.6618 | 1094074.6406 | 316559.8604 | 1410634.501 | 27783.2353
34 | 1063.736 | 763.736 | 1147.4583 | 83.7223 | 826.17 | 321.2883 | 826.17 | 644.4126 | 181.7574 | 0 | 965.7009 | 2634.5495 | 479 | 2624.7324 | 1600 | 2500 | 7272.7273 | 545.6654 | 75627.5498 | 99709.2077 | 151255.0995 | 20447.4486 | 18978.9137 | 3463.6517 | 137.8771 | 25.1626 | 53.1453 | 9.699 | 10870.2328 | 3623.4109 | 3774.9612 | 3774.9612 | 629.1602 | 629.1602 | 1089741.7806 | 315306.1895 | 1405047.9701 | 27604.0557
35 | 1059.7719 | 759.7719 | 1143.0785 | 83.3066 | 823.0165 | 320.062 | 823.0165 | 641.9529 | 181.0636 | 0 | 962.0149 | 2627.6196 | 479 | 2618.3187 | 1600 | 2500 | 7272.7273 | 545.6654 | 75154.7915 | 99214.138 | 150309.583 | 20319.6288 | 18860.2739 | 3442 | 137.3509 | 25.0665 | 52.851 | 9.6453 | 10828.7418 | 3609.5806 | 3760.5524 | 3760.5524 | 626.7587 | 626.7587 | 1085582.3033 | 314102.6852 | 1399684.9885 | 27431.4989
36 | 1055.9569 | 755.9569 | 1138.8616 | 82.9047 | 819.9803 | 318.8812 | 819.9803 | 639.5847 | 180.3957 | 0 | 958.4659 | 2620.8519 | 479 | 2612.0544 | 1600 | 2500 | 7272.7273 | 545.6654 | 74698.3939 | 98735.4886 | 149396.7879 | 20196.2324 | 18745.7398 | 3421.0975 | 136.8442 | 24.9741 | 52.5677 | 9.5936 | 10788.7937 | 3596.2646 | 3746.6794 | 3746.6794 | 624.4466 | 624.4466 | 1081577.5049 | 312943.9357 | 1394521.4407 | 27264.9138
37 | 1052.2805 | 752.2805 | 1134.796 | 82.5155 | 817.0531 | 317.7429 | 817.0531 | 637.3014 | 179.7517 | 0 | 955.0443 | 2614.2324 | 479 | 2605.9261 | 1600 | 2500 | 7272.7273 | 545.6654 | 74257.101 | 98271.9992 | 148514.2019 | 20076.9199 | 18634.9963 | 3400.8868 | 136.3556 | 24.8849 | 52.2945 | 9.5438 | 10750.2789 | 3583.4263 | 3733.3042 | 3733.3042 | 622.2174 | 622.2174 | 1077716.3928 | 311826.7605 | 1389543.1533 | 27103.8419
38 | 1048.7356 | 748.7356 | 1130.8741 | 82.1385 | 814.2293 | 316.6447 | 814.2293 | 635.0989 | 179.1305 | 0 | 951.7436 | 2607.7586 | 479 | 2599.9318 | 1600 | 2500 | 7272.7273 | 545.6654 | 73830.2445 | 97822.9989 | 147660.489 | 19961.5106 | 18527.8756 | 3381.3373 | 135.8844 | 24.7989 | 52.031 | 9.4957 | 10713.1256 | 3571.0419 | 3720.4017 | 3720.4017 | 620.067 | 620.067 | 1073991.7635 | 310749.0752 | 1384740.8386 | 26948.0392
39 | 1045.3123 | 745.3123 | 1127.085 | 81.7727 | 811.5012 | 315.5838 | 811.5012 | 632.971 | 178.5303 | 0 | 948.5548 | 2601.4201 | 479 | 2594.0618 | 1600 | 2500 | 7272.7273 | 545.6654 | 73416.7431 | 97387.4022 | 146833.4861 | 19849.712 | 18424.1065 | 3362.3994 | 135.4291 | 24.7158 | 51.7765 | 9.4492 | 10677.2309 | 3559.077 | 3707.9364 | 3707.9364 | 617.9894 | 617.9894 | 1070393.3169 | 309707.8997 | 1380101.2166 | 26797.1112
40 | 1042.005 | 742.005 | 1123.4227 | 81.4177 | 808.8644 | 314.5584 | 808.8644 | 630.9142 | 177.9502 | 0 | 945.4726 | 2595.2122 | 479 | 2588.3119 | 1600 | 2500 | 7272.7273 | 545.6654 | 73015.9789 | 96964.5892 | 146031.9578 | 19741.3573 | 18323.5338 | 3344.0449 | 134.989 | 24.6355 | 51.5304 | 9.4043 | 10642.5365 | 3547.5122 | 3695.8879 | 3695.8879 | 615.9813 | 615.9813 | 1066915.2006 | 308701.5405 | 1375616.7411 | 26650.8323
41 | 1038.8067 | 738.8067 | 1119.8795 | 81.0728 | 806.3133 | 313.5663 | 806.3133 | 628.9243 | 177.3889 | 0 | 942.4906 | 2589.1296 | 479 | 2582.6772 | 1600 | 2500 | 7272.7273 | 545.6654 | 72627.2392 | 96553.8442 | 145254.4785 | 19636.2536 | 18225.9786 | 3326.2411 | 134.5633 | 24.5578 | 51.2923 | 9.3609 | 10608.9708 | 3536.3236 | 3684.2314 | 3684.2314 | 614.0386 | 614.0386 | 1063550.2393 | 307727.9217 | 1371278.161 | 26508.9423
42 | 1035.7132 | 735.7132 | 1116.4509 | 80.7377 | 803.8447 | 312.6063 | 803.8447 | 626.9988 | 176.8458 | 0 | 939.6051 | 2583.1692 | 479 | 2577.1547 | 1600 | 2500 | 7272.7273 | 545.6654 | 72250.0637 | 96154.7052 | 144500.1273 | 19534.2765 | 18131.3255 | 3308.9669 | 134.1513 | 24.4826 | 51.062 | 9.3188 | 10576.4904 | 3525.4968 | 3672.9518 | 3672.9518 | 612.1586 | 612.1586 | 1060294.0776 | 306785.7829 | 1367079.8605 | 26371.2732
43 | 1032.7196 | 732.7196 | 1113.1314 | 80.4118 | 801.4546 | 311.6768 | 801.4546 | 625.1346 | 176.32 | 0 | 936.8114 | 2577.3242 | 479 | 2571.7384 | 1600 | 2500 | 7272.7273 | 545.6654 | 71883.8479 | 95766.5659 | 143767.6958 | 19435.2626 | 18039.4228 | 3292.1947 | 133.7525 | 24.4098 | 50.8389 | 9.2781 | 10545.0435 | 3515.0145 | 3662.031 | 3662.031 | 610.3385 | 610.3385 | 1057141.5192 | 305873.6208 | 1363015.14 | 26237.6045
44 | 1029.8214 | 729.8214 | 1109.9162 | 80.0947 | 799.1397 | 310.7765 | 799.1397 | 623.3289 | 175.8107 | 0 | 934.1055 | 2571.5926 | 479 | 2566.4262 | 1600 | 2500 | 7272.7273 | 545.6654 | 71528.1647 | 95388.9973 | 143056.3293 | 19339.0964 | 17950.1632 | 3275.9048 | 133.3661 | 24.3393 | 50.6229 | 9.2387 | 10514.5849 | 3504.8616 | 3651.4535 | 3651.4535 | 608.5756 | 608.5756 | 1054088.0492 | 304990.129 | 1359078.1782 | 26107.7801
45 | 1027.0139 | 727.0139 | 1106.8 | 79.7861 | 796.896 | 309.904 | 796.896 | 621.5789 | 175.3171 | 0 | 931.4829 | 2565.9684 | 479 | 2561.2129 | 1600 | 2500 | 7272.7273 | 545.6654 | 71182.4519 | 95021.4354 | 142364.9039 | 19245.6259 | 17863.4058 | 3260.0716 | 132.9917 | 24.271 | 50.4136 | 9.2005 | 10485.0645 | 3495.0215 | 3641.2018 | 3641.2018 | 606.867 | 606.867 | 1051128.6236 | 304133.8479 | 1355262.4716 | 25981.595
46 | 1024.2901 | 724.2901 | 1103.7754 | 79.4853 | 794.7183 | 309.0571 | 794.7183 | 619.8803 | 174.838 | 0 | 928.9374 | 2560.446 | 479 | 2556.0932 | 1600 | 2500 | 7272.7273 | 545.6654 | 70846.029 | 94663.1967 | 141692.058 | 19154.6671 | 17778.9797 | 3244.6638 | 132.6283 | 24.2047 | 50.2103 | 9.1634 | 10456.4117 | 3485.4706 | 3631.2514 | 3631.2514 | 605.2086 | 605.2086 | 1048256.176 | 303302.7332 | 1351558.9092 | 25858.8006
47 | 1021.6505 | 721.6505 | 1100.8428 | 79.1923 | 792.6068 | 308.236 | 792.6068 | 618.2333 | 174.3735 | 0 | 926.4693 | 2555.0268 | 479 | 2551.0683 | 1600 | 2500 | 7272.7273 | 545.6654 | 70518.8958 | 94314.2814 | 141037.7915 | 19066.22 | 17696.8848 | 3229.6815 | 132.2759 | 24.1403 | 50.0133 | 9.1274 | 10428.6301 | 3476.21 | 3621.6035 | 3621.6035 | 603.6006 | 603.6006 | 1045471.0678 | 302496.8892 | 1347967.957 | 25739.397
48 | 1019.0811 | 719.0811 | 1097.9871 | 78.906 | 790.5507 | 307.4364 | 790.5507 | 616.6296 | 173.9212 | 0 | 924.0659 | 2549.6949 | 479 | 2546.1236 | 1600 | 2500 | 7272.7273 | 545.6654 | 70199.6312 | 93973.2628 | 140399.2624 | 18979.9003 | 17616.7646 | 3215.0595 | 131.9327 | 24.0777 | 49.8214 | 9.0924 | 10401.5769 | 3467.1923 | 3612.2086 | 3612.2086 | 602.0348 | 602.0348 | 1042758.9804 | 301712.1731 | 1344471.1535 | 25622.8654
49 | 1016.586 | 716.586 | 1095.2126 | 78.6266 | 788.5531 | 306.6595 | 788.5531 | 615.0714 | 173.4817 | 0 | 921.7309 | 2544.4558 | 479 | 2541.2642 | 1600 | 2500 | 7272.7273 | 545.6654 | 69888.604 | 93640.5113 | 139777.2081 | 18895.8078 | 17538.7116 | 3200.8149 | 131.5994 | 24.0169 | 49.635 | 9.0584 | 10375.2932 | 3458.4311 | 3603.081 | 3603.081 | 600.5135 | 600.5135 | 1040124.0444 | 300949.7799 | 1341073.8243 | 25509.3405
50 | 1013.1085 | 713.1085 | 1091.3802 | 78.2717 | 785.7938 | 305.5865 | 785.7938 | 612.9191 | 172.8746 | 0 | 918.5056 | 2538.3216 | 479 | 2535.5733 | 1600 | 2500 | 7272.7273 | 545.6654 | 69488.0865 | 93217.8816 | 138976.173 | 18787.5197 | 17438.2008 | 3182.4716 | 131.1389 | 23.9328 | 49.3775 | 9.0114 | 10338.9879 | 3446.3293 | 3590.473 | 3590.473 | 598.4122 | 598.4122 | 1036484.4261 | 299896.6918 | 1336381.1179 | 25363.1516
51 | 1006.243 | 706.243 | 1084.2127 | 77.9697 | 780.6331 | 303.5796 | 780.6331 | 608.8939 | 171.7393 | 0 | 912.4734 | 2542.5639 | 479 | 2539.503 | 1600 | 2500 | 7272.7273 | 545.6654 | 69138.7192 | 92858.1786 | 138277.4383 | 18693.0611 | 17350.5262 | 3166.471 | 130.2776 | 23.7757 | 48.896 | 8.9235 | 10271.0877 | 3423.6959 | 3566.893 | 3566.893 | 594.4822 | 594.4822 | 1029677.431 | 297927.1539 | 1327604.5849 | 25235.6325
52 | 1004.0167 | 704.0167 | 1081.7844 | 77.7677 | 778.8848 | 302.8996 | 778.8848 | 607.5301 | 171.3546 | 0 | 910.4298 | 2539.5112 | 479 | 2536.6708 | 1600 | 2500 | 7272.7273 | 545.6654 | 68906.9355 | 92617.6559 | 137813.871 | 18630.3937 | 17292.3595 | 3155.8556 | 129.9858 | 23.7224 | 48.7328 | 8.8937 | 10248.0836 | 3416.0279 | 3558.9042 | 3558.9042 | 593.1507 | 593.1507 | 1027371.2665 | 297259.8876 | 1324631.1541 | 25151.0315
53 | 1001.8477 | 701.8477 | 1079.4184 | 77.5707 | 777.1812 | 302.2371 | 777.1812 | 606.2014 | 170.9799 | 0 | 908.4385 | 2536.518 | 479 | 2533.8937 | 1600 | 2500 | 7272.7273 | 545.6654 | 68680.9516 | 92382.9558 | 137361.9032 | 18569.2943 | 17235.6483 | 3145.5058 | 129.7015 | 23.6705 | 48.5738 | 8.8647 | 10225.6696 | 3408.5565 | 3551.1204 | 3551.1204 | 591.8534 | 591.8534 | 1025124.2595 | 296609.738 | 1321733.9976 | 25068.5473
54 | 999.7363 | 699.7363 | 1077.1149 | 77.3785 | 775.5227 | 301.5922 | 775.5227 | 604.9077 | 170.615 | 0 | 906.4999 | 2533.5862 | 479 | 2531.1735 | 1600 | 2500 | 7272.7273 | 545.6654 | 68460.8107 | 92154.1217 | 136921.6214 | 18509.7747 | 17180.4034 | 3135.4236 | 129.4248 | 23.62 | 48.4191 | 8.8365 | 10203.8478 | 3401.2826 | 3543.5422 | 3543.5422 | 590.5904 | 590.5904 | 1022936.6211 | 295976.7661 | 1318913.3872 | 24988.1959
55 | 997.6799 | 697.6799 | 1074.8709 | 77.191 | 773.907 | 300.9638 | 773.907 | 603.6475 | 170.2595 | 0 | 904.6113 | 2530.7105 | 479 | 2528.5051 | 1600 | 2500 | 7272.7273 | 545.6654 | 68246.1628 | 91930.8026 | 136492.3256 | 18451.7403 | 17126.537 | 3125.593 | 129.1551 | 23.5708 | 48.2683 | 8.809 | 10182.5898 | 3394.1966 | 3536.1599 | 3536.1599 | 589.36 | 589.36 | 1020805.5053 | 295360.1484 | 1316165.6537 | 24909.8494
56 | 995.6756 | 695.6756 | 1072.6836 | 77.008 | 772.3322 | 300.3514 | 772.3322 | 602.4191 | 169.9131 | 0 | 902.7705 | 2527.8901 | 479 | 2525.8879 | 1600 | 2500 | 7272.7273 | 545.6654 | 68036.79 | 91712.7795 | 136073.5799 | 18395.1321 | 17073.9944 | 3116.004 | 128.8923 | 23.5228 | 48.1213 | 8.7821 | 10161.8688 | 3387.2896 | 3528.964 | 3528.964 | 588.1607 | 588.1607 | 1018728.2295 | 294759.1089 | 1313487.3384 | 24833.4283
57 | 993.7244 | 693.7244 | 1070.5538 | 76.8294 | 770.7987 | 299.7551 | 770.7987 | 601.223 | 169.5757 | 0 | 900.9781 | 2525.125 | 479 | 2523.3218 | 1600 | 2500 | 7272.7273 | 545.6654 | 67832.7211 | 91500.0814 | 135665.4422 | 18339.9579 | 17022.7829 | 3106.6579 | 128.6364 | 23.4761 | 47.9782 | 8.756 | 10141.6924 | 3380.5641 | 3521.9572 | 3521.9572 | 586.9929 | 586.9929 | 1016705.536 | 294173.8622 | 1310879.3982 | 24758.9432
58 | 991.8212 | 691.8212 | 1068.476 | 76.6549 | 769.3027 | 299.1733 | 769.3027 | 600.0561 | 169.2466 | 0 | 899.2294 | 2522.4112 | 479 | 2520.8033 | 1600 | 2500 | 7272.7273 | 545.6654 | 67633.4988 | 91292.2492 | 135266.9977 | 18286.0941 | 16972.7876 | 3097.5337 | 128.3867 | 23.4306 | 47.8386 | 8.7306 | 10122.0093 | 3374.0031 | 3515.1218 | 3515.1218 | 585.8536 | 585.8536 | 1014732.3067 | 293602.9275 | 1308335.2343 | 24686.2271
59 | 989.9647 | 689.9647 | 1066.449 | 76.4843 | 767.8433 | 298.6057 | 767.8433 | 598.9178 | 168.9255 | 0 | 897.5235 | 2519.7488 | 479 | 2518.3324 | 1600 | 2500 | 7272.7273 | 545.6654 | 67439.0221 | 91089.1813 | 134878.0443 | 18233.5134 | 16923.9832 | 3088.6269 | 128.1432 | 23.3861 | 47.7025 | 8.7057 | 10102.8068 | 3367.6023 | 3508.4532 | 3508.4532 | 584.7422 | 584.7422 | 1012807.2531 | 293045.9319 | 1305853.185 | 24615.2431
60 | 988.1585 | 688.1585 | 1064.4766 | 76.3181 | 766.4232 | 298.0535 | 766.4232 | 597.8101 | 168.6131 | 0 | 895.8635 | 2517.1427 | 479 | 2515.9137 | 1600 | 2500 | 7272.7273 | 545.6654 | 67249.6403 | 90891.2283 | 134499.2805 | 18182.3101 | 16876.4573 | 3079.9535 | 127.9062 | 23.3429 | 47.5699 | 8.6815 | 10084.1216 | 3361.3739 | 3501.9643 | 3501.9643 | 583.6607 | 583.6607 | 1010934.0573 | 292503.941 | 1303437.9983 | 24546.1187
61 | 986.3913 | 686.3913 | 1062.5465 | 76.1552 | 765.0335 | 297.513 | 765.0335 | 596.7261 | 168.3074 | 0 | 894.2391 | 2514.5768 | 479 | 2513.532 | 1600 | 2500 | 7272.7273 | 545.6654 | 67064.1577 | 90697.1902 | 134128.3154 | 18132.1612 | 16829.9101 | 3071.4586 | 127.6742 | 23.3005 | 47.4402 | 8.6578 | 10065.837 | 3355.279 | 3495.6145 | 3495.6145 | 582.6024 | 582.6024 | 1009101.0308 | 291973.5726 | 1301074.6034 | 24478.4176
62 | 984.6691 | 684.6691 | 1060.6652 | 75.9961 | 763.679 | 296.9863 | 763.679 | 595.6696 | 168.0094 | 0 | 892.6559 | 2512.0614 | 479 | 2511.1972 | 1600 | 2500 | 7272.7273 | 545.6654 | 66883.2323 | 90507.7273 | 133766.4647 | 18083.2443 | 16784.5064 | 3063.1724 | 127.4482 | 23.2593 | 47.3139 | 8.6348 | 10048.0151 | 3349.3384 | 3489.4254 | 3489.4254 | 581.5709 | 581.5709 | 1007314.3808 | 291456.6227 | 1298771.0035 | 24412.3798
63 | 982.9876 | 682.9876 | 1058.8281 | 75.8405 | 762.3563 | 296.4719 | 762.3563 | 594.6379 | 167.7184 | 0 | 891.1098 | 2509.5931 | 479 | 2508.906 | 1600 | 2500 | 7272.7273 | 545.6654 | 66706.4704 | 90322.4441 | 133412.9408 | 18035.4531 | 16740.1476 | 3055.0769 | 127.2274 | 23.219 | 47.1904 | 8.6123 | 10030.6116 | 3343.5372 | 3483.3816 | 3483.3816 | 580.5636 | 580.5636 | 1005569.6802 | 290951.8106 | 1296521.4908 | 24347.8617
64 | 981.3437 | 681.3437 | 1057.0317 | 75.6881 | 761.0628 | 295.9689 | 761.0628 | 593.629 | 167.4338 | 0 | 889.5979 | 2507.1618 | 479 | 2506.649 | 1600 | 2500 | 7272.7273 | 545.6654 | 66533.3897 | 90140.8571 | 133066.7794 | 17988.6572 | 16696.7126 | 3047.15 | 127.0116 | 23.1796 | 47.0697 | 8.5902 | 10013.5938 | 3337.8646 | 3477.4718 | 3477.4718 | 579.5786 | 579.5786 | 1003863.6424 | 290458.1851 | 1294321.8275 | 24284.6872
65 | 979.7406 | 679.7406 | 1055.2798 | 75.5392 | 759.8015 | 295.4783 | 759.8015 | 592.6451 | 167.1563 | 0 | 888.1235 | 2504.7811 | 479 | 2504.4388 | 1600 | 2500 | 7272.7273 | 545.6654 | 66364.5504 | 89963.5281 | 132729.1009 | 17943.0081 | 16654.3419 | 3039.4174 | 126.8011 | 23.1412 | 46.952 | 8.5687 | 9996.9972 | 3332.3324 | 3471.7082 | 3471.7082 | 578.618 | 578.618 | 1002199.8295 | 289976.7771 | 1292176.6066 | 24223.0609
66 | 978.1762 | 678.1762 | 1053.5697 | 75.3935 | 758.5702 | 294.9995 | 758.5702 | 591.6848 | 166.8854 | 0 | 886.6843 | 2502.4413 | 479 | 2502.2666 | 1600 | 2500 | 7272.7273 | 545.6654 | 66199.5386 | 89790.0418 | 132399.0772 | 17898.3938 | 16612.9318 | 3031.8601 | 126.5956 | 23.1037 | 46.8371 | 8.5478 | 9980.797 | 3326.9323 | 3466.0823 | 3466.0823 | 577.6804 | 577.6804 | 1000575.763 | 289506.8692 | 1290082.6322 | 24162.8316
67 | 976.6445 | 676.6445 | 1051.8952 | 75.2507 | 757.3646 | 294.5307 | 757.3646 | 590.7444 | 166.6202 | 0 | 885.275 | 2500.141 | 479 | 2500.1309 | 1600 | 2500 | 7272.7273 | 545.6654 | 66037.9127 | 89619.9546 | 132075.8254 | 17854.6949 | 16572.3714 | 3024.4578 | 126.3944 | 23.067 | 46.7246 | 8.5272 | 9964.9342 | 3321.6447 | 3460.5735 | 3460.5735 | 576.7622 | 576.7622 | 998985.5102 | 289046.745 | 1288032.2552 | 24103.8381
68 | 975.144 | 675.144 | 1050.2545 | 75.1105 | 756.1832 | 294.0713 | 756.1832 | 589.8229 | 166.3603 | 0 | 883.8942 | 2497.8725 | 479 | 2498.0246 | 1600 | 2500 | 7272.7273 | 545.6654 | 65879.3581 | 89452.9511 | 131758.7162 | 17811.8265 | 16532.5818 | 3017.1962 | 126.1972 | 23.031 | 46.6144 | 8.5071 | 9949.3907 | 3316.4636 | 3455.1756 | 3455.1756 | 575.8626 | 575.8626 | 997427.2727 | 288595.8841 | 1286023.1568 | 24045.9657
69 | 973.6803 | 673.6803 | 1048.6537 | 74.9734 | 755.0307 | 293.623 | 755.0307 | 588.9239 | 166.1068 | 0 | 882.547 | 2495.6489 | 479 | 2495.9599 | 1600 | 2500 | 7272.7273 | 545.6654 | 65724.5811 | 89289.74 | 131449.1622 | 17769.9793 | 16493.7401 | 3010.1076 | 126.0049 | 22.9959 | 46.5068 | 8.4875 | 9934.2265 | 3311.4088 | 3449.9095 | 3449.9095 | 574.9849 | 574.9849 | 995907.0604 | 288156.0255 | 1284063.0859 | 23989.4721
70 | 972.2491 | 672.2491 | 1047.0882 | 74.8391 | 753.9035 | 293.1847 | 753.9035 | 588.0448 | 165.8588 | 0 | 881.2295 | 2493.4622 | 479 | 2493.9295 | 1600 | 2500 | 7272.7273 | 545.6654 | 65573.0755 | 89129.8133 | 131146.1511 | 17729.0167 | 16455.7194 | 3003.1688 | 125.8168 | 22.9616 | 46.4016 | 8.4683 | 9919.396 | 3306.4653 | 3444.7592 | 3444.7592 | 574.1265 | 574.1265 | 994420.3021 | 287725.8464 | 1282146.1485 | 23934.1726
71 | 970.8509 | 670.8509 | 1045.5586 | 74.7076 | 752.8022 | 292.7564 | 752.8022 | 587.1857 | 165.6165 | 0 | 879.9421 | 2491.3123 | 479 | 2491.9331 | 1600 | 2500 | 7272.7273 | 545.6654 | 65424.8658 | 88973.1956 | 130849.7316 | 17688.9452 | 16418.5258 | 2996.381 | 125.633 | 22.928 | 46.2989 | 8.4495 | 9904.9049 | 3301.635 | 3439.7268 | 3439.7268 | 573.2878 | 573.2878 | 992967.5686 | 287305.5121 | 1280273.0807 | 23880.076
72 | 969.481 | 669.481 | 1044.0595 | 74.5785 | 751.7228 | 292.3367 | 751.7228 | 586.3438 | 165.379 | 0 | 878.6805 | 2489.1932 | 479 | 2489.9652 | 1600 | 2500 | 7272.7273 | 545.6654 | 65279.4709 | 88819.4041 | 130558.9419 | 17649.6347 | 16382.0387 | 2989.7221 | 125.4529 | 22.8951 | 46.1981 | 8.4312 | 9890.7038 | 3296.9013 | 3434.7952 | 3434.7952 | 572.4659 | 572.4659 | 991543.9141 | 286893.5915 | 1278437.5057 | 23827.0069
73 | 968.1476 | 668.1476 | 1042.5999 | 74.4523 | 750.6719 | 291.928 | 750.6719 | 585.5241 | 165.1478 | 0 | 877.4521 | 2487.1113 | 479 | 2488.0317 | 1600 | 2500 | 7272.7273 | 545.6654 | 65137.5893 | 88669.1403 | 130275.1787 | 17611.2742 | 16346.4331 | 2983.224 | 125.2775 | 22.8631 | 46.1001 | 8.4133 | 9876.8763 | 3292.2921 | 3429.9932 | 3429.9932 | 571.6655 | 571.6655 | 990157.7063 | 286492.5058 | 1276650.2121 | 23775.2201
74 | 967.0361 | 667.0361 | 1041.3709 | 74.3348 | 749.7871 | 291.5839 | 749.7871 | 584.8339 | 164.9532 | 0 | 876.4178 | 2484.854 | 479 | 2485.9351 | 1600 | 2500 | 7272.7273 | 545.6654 | 65005.985 | 88529.2332 | 130011.97 | 17575.6922 | 16313.4067 | 2977.1967 | 125.1298 | 22.8362 | 46.0175 | 8.3982 | 9865.234 | 3288.4113 | 3425.9501 | 3425.9501 | 570.9917 | 570.9917 | 988990.5582 | 286154.8028 | 1275145.361 | 23727.1845
75 | 965.954 | 665.954 | 1040.1737 | 74.2198 | 748.9251 | 291.2486 | 748.9251 | 584.1616 | 164.7635 | 0 | 875.4102 | 2482.6264 | 479 | 2483.866 | 1600 | 2500 | 7272.7273 | 545.6654 | 64877.2071 | 88392.1641 | 129754.4142 | 17540.8745 | 16281.0896 | 2971.2989 | 124.986 | 22.8099 | 45.9371 | 8.3835 | 9853.8925 | 3284.6308 | 3422.0115 | 3422.0115 | 570.3352 | 570.3352 | 987853.5713 | 285825.8267 | 1273679.398 | 23680.1806
76 | 964.8892 | 664.8892 | 1038.9954 | 74.1062 | 748.0767 | 290.9187 | 748.0767 | 583.4998 | 164.5769 | 0 | 874.4185 | 2480.4195 | 479 | 2481.8161 | 1600 | 2500 | 7272.7273 | 545.6654 | 64750.2275 | 88256.9002 | 129500.455 | 17506.543 | 16249.2238 | 2965.4833 | 124.8444 | 22.7841 | 45.8579 | 8.3691 | 9842.7295 | 3280.9098 | 3418.1349 | 3418.1349 | 569.6891 | 569.6891 | 986734.4834 | 285502.0295 | 1272236.5129 | 23633.833
77 | 963.8475 | 663.8475 | 1037.8421 | 73.9946 | 747.2463 | 290.5958 | 747.2463 | 582.8521 | 164.3942 | 0 | 873.4479 | 2478.2413 | 479 | 2479.7926 | 1600 | 2500 | 7272.7273 | 545.6654 | 64625.626 | 88124.0237 | 129251.252 | 17472.8544 | 16217.9547 | 2959.7767 | 124.7058 | 22.7588 | 45.7804 | 8.3549 | 9831.8047 | 3277.2682 | 3414.3409 | 3414.3409 | 569.0568 | 569.0568 | 985639.2692 | 285185.1399 | 1270824.4092 | 23588.3535
78 | 962.8257 | 662.8257 | 1036.7104 | 73.8847 | 746.4315 | 290.2789 | 746.4315 | 582.2166 | 164.2149 | 0 | 872.4955 | 2476.0867 | 479 | 2477.7909 | 1600 | 2500 | 7272.7273 | 545.6654 | 64503.0469 | 87993.1774 | 129006.0938 | 17439.7127 | 16187.1932 | 2954.1628 | 124.5698 | 22.734 | 45.7044 | 8.341 | 9821.0837 | 3273.6946 | 3410.6178 | 3410.6178 | 568.4363 | 568.4363 | 984564.4845 | 284874.1614 | 1269438.646 | 23543.6121
79 | 961.8219 | 661.8219 | 1035.5984 | 73.7764 | 745.6308 | 289.9675 | 745.6308 | 581.5921 | 164.0388 | 0 | 871.5596 | 2473.9538 | 479 | 2475.8094 | 1600 | 2500 | 7272.7273 | 545.6654 | 64382.328 | 87864.1986 | 128764.656 | 17407.0739 | 16156.8985 | 2948.634 | 124.4362 | 22.7096 | 45.6297 | 8.3274 | 9810.549 | 3270.183 | 3406.9594 | 3406.9594 | 567.8266 | 567.8266 | 983508.3865 | 284568.5898 | 1268076.9763 | 23499.5497
80 | 960.8353 | 660.8353 | 1034.5049 | 73.6696 | 744.8435 | 289.6614 | 744.8435 | 580.978 | 163.8656 | 0 | 870.6393 | 2471.8415 | 479 | 2473.8467 | 1600 | 2500 | 7272.7273 | 545.6654 | 64263.3644 | 87736.9818 | 128526.7289 | 17374.9096 | 16127.0443 | 2943.1856 | 124.3048 | 22.6856 | 45.5562 | 8.314 | 9800.1903 | 3266.7301 | 3403.362 | 3403.362 | 567.227 | 567.227 | 982469.9223 | 284268.1202 | 1266738.0426 | 23456.128
81 | 959.86 | 659.86 | 1033.4239 | 73.5638 | 744.0652 | 289.3587 | 744.0652 | 580.3708 | 163.6943 | 0 | 869.7295 | 2469.7433 | 479 | 2471.8971 | 1600 | 2500 | 7272.7273 | 545.6654 | 64145.6168 | 87610.9856 | 128291.2337 | 17343.0742 | 16097.4953 | 2937.7929 | 124.1749 | 22.6619 | 45.4836 | 8.3007 | 9789.9491 | 3263.3164 | 3399.8055 | 3399.8055 | 566.6343 | 566.6343 | 981443.2413 | 283971.0601 | 1265414.3013 | 23413.1501
82 | 958.9009 | 658.9009 | 1032.3603 | 73.4594 | 743.2994 | 289.0609 | 743.2994 | 579.7735 | 163.5259 | 0 | 868.8344 | 2467.6632 | 479 | 2469.9641 | 1600 | 2500 | 7272.7273 | 545.6654 | 64029.4895 | 87486.616 | 128058.979 | 17311.6768 | 16068.3528 | 2932.4744 | 124.0471 | 22.6386 | 45.4121 | 8.2877 | 9779.8734 | 3259.9578 | 3396.3065 | 3396.3065 | 566.0511 | 566.0511 | 980433.1481 | 283678.7994 | 1264111.9475 | 23370.7637
83 | 957.9603 | 657.9603 | 1031.3169 | 73.3566 | 742.5482 | 288.7687 | 742.5482 | 579.1876 | 163.3606 | 0 | 867.9563 | 2465.6069 | 479 | 2468.0533 | 1600 | 2500 | 7272.7273 | 545.6654 | 63915.2907 | 87364.1824 | 127830.5815 | 17280.8008 | 16039.6944 | 2927.2442 | 123.9217 | 22.6157 | 45.342 | 8.2749 | 9769.9891 | 3256.663 | 3392.8739 | 3392.8739 | 565.479 | 565.479 | 979442.2509 | 283392.093 | 1262834.3439 | 23329.0811
84 | 957.0401 | 657.0401 | 1030.2957 | 73.2555 | 741.8129 | 288.4828 | 741.8129 | 578.6141 | 163.1988 | 0 | 867.0968 | 2463.5753 | 479 | 2466.1651 | 1600 | 2500 | 7272.7273 | 545.6654 | 63803.1515 | 87243.8165 | 127606.303 | 17250.4817 | 16011.5528 | 2922.1084 | 123.799 | 22.5933 | 45.2734 | 8.2624 | 9760.3147 | 3253.4382 | 3389.5143 | 3389.5143 | 564.919 | 564.919 | 978472.3963 | 283111.4749 | 1261583.8713 | 23288.1503
85 | 956.1299 | 656.1299 | 1029.2852 | 73.1553 | 741.0853 | 288.1999 | 741.0853 | 578.0466 | 163.0388 | 0 | 866.2464 | 2461.5546 | 479 | 2464.2871 | 1600 | 2500 | 7272.7273 | 545.6654 | 63692.0368 | 87124.4789 | 127384.0735 | 17220.4396 | 15983.6683 | 2917.0195 | 123.6776 | 22.5712 | 45.2055 | 8.25 | 9750.7422 | 3250.2474 | 3386.19 | 3386.19 | 564.365 | 564.365 | 977512.7456 | 282833.8093 | 1260346.555 | 23247.5934
86 | 955.2288 | 655.2288 | 1028.2848 | 73.056 | 740.3651 | 287.9197 | 740.3651 | 577.4847 | 162.8803 | 0 | 865.4045 | 2459.5473 | 479 | 2462.4213 | 1600 | 2500 | 7272.7273 | 545.6654 | 63581.9556 | 87006.1786 | 127163.9111 | 17190.6769 | 15956.0431 | 2911.9779 | 123.5574 | 22.5492 | 45.1383 | 8.2377 | 9741.2652 | 3247.0884 | 3382.8988 | 3382.8988 | 563.8165 | 563.8165 | 976562.6739 | 282558.9153 | 1259121.5892 | 23207.4138
87 | 954.3492 | 654.3492 | 1027.3076 | 72.9585 | 739.6615 | 287.6461 | 739.6615 | 576.936 | 162.7255 | 0 | 864.5821 | 2457.5656 | 479 | 2460.5792 | 1600 | 2500 | 7272.7273 | 545.6654 | 63474.016 | 86890.0284 | 126948.0319 | 17161.4932 | 15928.9554 | 2907.0344 | 123.44 | 22.5278 | 45.0726 | 8.2258 | 9732.0082 | 3244.0027 | 3379.6841 | 3379.6841 | 563.2807 | 563.2807 | 975634.6662 | 282290.4053 | 1257925.0715 | 23168.0158
88 | 953.4836 | 653.4836 | 1026.3457 | 72.8621 | 738.9689 | 287.3768 | 738.9689 | 576.3957 | 162.5732 | 0 | 863.7725 | 2455.5982 | 479 | 2458.7503 | 1600 | 2500 | 7272.7273 | 545.6654 | 63367.4446 | 86775.2519 | 126734.8892 | 17132.6795 | 15902.2111 | 2902.1535 | 123.3244 | 22.5067 | 45.008 | 8.214 | 9722.8952 | 3240.9651 | 3376.5194 | 3376.5194 | 562.7532 | 562.7532 | 974721.0846 | 282026.0694 | 1256747.1539 | 23129.1173
89 | 952.6332 | 652.6332 | 1025.4003 | 72.7671 | 738.2882 | 287.1121 | 738.2882 | 575.8648 | 162.4234 | 0 | 862.9769 | 2453.6509 | 479 | 2456.94 | 1600 | 2500 | 7272.7273 | 545.6654 | 63262.464 | 86662.0723 | 126524.928 | 17104.2958 | 15875.866 | 2897.3455 | 123.2108 | 22.486 | 44.9445 | 8.2024 | 9713.9394 | 3237.9798 | 3373.4093 | 3373.4093 | 562.2349 | 562.2349 | 973823.2607 | 281766.2928 | 1255589.5534 | 23090.7994
90 | 951.7971 | 651.7971 | 1024.4703 | 72.6732 | 737.6186 | 286.8517 | 737.6186 | 575.3425 | 162.2761 | 0 | 862.1942 | 2451.7205 | 479 | 2455.1453 | 1600 | 2500 | 7272.7273 | 545.6654 | 63158.9204 | 86550.3353 | 126317.8407 | 17076.3007 | 15849.8814 | 2892.6034 | 123.0991 | 22.4656 | 44.882 | 8.191 | 9705.1294 | 3235.0431 | 3370.3498 | 3370.3498 | 561.725 | 561.725 | 972940.061 | 281510.7475 | 1254450.8085 | 23053.0059
91 | 950.9755 | 650.9755 | 1023.5561 | 72.5807 | 736.9604 | 286.5957 | 736.9604 | 574.8291 | 162.1313 | 0 | 861.4248 | 2449.8087 | 479 | 2453.3678 | 1600 | 2500 | 7272.7273 | 545.6654 | 63056.872 | 86440.0993 | 126113.744 | 17048.7098 | 15824.2722 | 2887.9297 | 122.9892 | 22.4455 | 44.8206 | 8.1798 | 9696.4689 | 3232.1563 | 3367.3422 | 3367.3422 | 561.2237 | 561.2237 | 972071.8414 | 281259.5366 | 1253331.378 | 23015.7583
92 | 950.1714 | 650.1714 | 1022.661 | 72.4896 | 736.3159 | 286.3451 | 736.3159 | 574.3264 | 161.9895 | 0 | 860.6715 | 2447.9199 | 479 | 2451.6116 | 1600 | 2500 | 7272.7273 | 545.6654 | 62956.6294 | 86331.6761 | 125913.2589 | 17021.6072 | 15799.1161 | 2883.3387 | 122.8816 | 22.4259 | 44.7604 | 8.1688 | 9687.9893 | 3229.3298 | 3364.3974 | 3364.3974 | 560.7329 | 560.7329 | 971221.7626 | 281013.5746 | 1252235.3372 | 22979.1697
93 | 949.3825 | 649.3825 | 1021.7824 | 72.3999 | 735.6833 | 286.0991 | 735.6833 | 573.833 | 161.8503 | 0 | 859.932 | 2446.05 | 479 | 2449.8727 | 1600 | 2500 | 7272.7273 | 545.6654 | 62857.9238 | 86224.7958 | 125715.8475 | 16994.9201 | 15774.3456 | 2878.8181 | 122.7761 | 22.4066 | 44.7014 | 8.158 | 9679.6656 | 3226.5552 | 3361.5068 | 3361.5068 | 560.2511 | 560.2511 | 970387.3102 | 280772.1339 | 1251159.444 | 22943.1422
94 | 948.6012 | 648.6012 | 1020.912 | 72.3108 | 735.0566 | 285.8554 | 735.0566 | 573.3442 | 161.7125 | 0 | 859.1995 | 2444.1884 | 479 | 2448.1415 | 1600 | 2500 | 7272.7273 | 545.6654 | 62759.9972 | 86118.6977 | 125519.9944 | 16968.4437 | 15749.7707 | 2874.3332 | 122.6715 | 22.3875 | 44.6429 | 8.1473 | 9671.42 | 3223.8067 | 3358.6433 | 3358.6433 | 559.7739 | 559.7739 | 969560.6919 | 280532.9599 | 1250093.6518 | 22907.399
95 | 947.8385 | 647.8385 | 1020.0618 | 72.2233 | 734.4445 | 285.6173 | 734.4445 | 572.8667 | 161.5778 | 0 | 858.484 | 2442.3498 | 479 | 2446.4316 | 1600 | 2500 | 7272.7273 | 545.6654 | 62663.9329 | 86014.4691 | 125327.8658 | 16942.4708 | 15725.6632 | 2869.9335 | 122.5693 | 22.3689 | 44.5858 | 8.1369 | 9663.3656 | 3221.1219 | 3355.8462 | 3355.8462 | 559.3077 | 559.3077 | 968753.2315 | 280299.3291 | 1249052.5605 | 22872.3355
96 | 947.0817 | 647.0817 | 1019.218 | 72.1363 | 733.837 | 285.381 | 733.837 | 572.3928 | 161.4441 | 0 | 857.7739 | 2440.5201 | 479 | 2444.7299 | 1600 | 2500 | 7272.7273 | 545.6654 | 62568.5489 | 85910.9232 | 125137.0978 | 16916.6817 | 15701.7263 | 2865.5651 | 122.4679 | 22.3504 | 44.5291 | 8.1266 | 9655.3728 | 3218.4576 | 3353.0705 | 3353.0705 | 558.8451 | 558.8451 | 967951.9531 | 280067.487 | 1248019.4401 | 22837.5203
97 | 946.339 | 646.339 | 1018.3896 | 72.0506 | 733.2405 | 285.1491 | 733.2405 | 571.9276 | 161.3129 | 0 | 857.0767 | 2438.7071 | 479 | 2443.0435 | 1600 | 2500 | 7272.7273 | 545.6654 | 62474.568 | 85808.786 | 124949.1359 | 16891.2721 | 15678.1416 | 2861.2608 | 122.3684 | 22.3322 | 44.4734 | 8.1164 | 9647.5247 | 3215.8416 | 3350.3451 | 3350.3451 | 558.3908 | 558.3908 | 967165.1845 | 279839.8432 | 1247005.0277 | 22803.2173
98 | 945.6076 | 645.6076 | 1017.5734 | 71.9658 | 732.6529 | 284.9206 | 732.6529 | 571.4692 | 161.1836 | 0 | 856.3898 | 2436.9072 | 479 | 2441.3693 | 1600 | 2500 | 7272.7273 | 545.6654 | 62381.7196 | 85707.7858 | 124763.4392 | 16866.1686 | 15654.8411 | 2857.0085 | 122.2703 | 22.3143 | 44.4186 | 8.1064 | 9639.7927 | 3213.2642 | 3347.66 | 3347.66 | 557.9433 | 557.9433 | 966390.0534 | 279615.5665 | 1246005.6199 | 22769.3276
99 | 944.8876 | 644.8876 | 1016.7696 | 71.882 | 732.0741 | 284.6955 | 732.0741 | 571.0178 | 161.0563 | 0 | 855.7133 | 2435.1231 | 479 | 2439.7097 | 1600 | 2500 | 7272.7273 | 545.6654 | 62290.0693 | 85607.9882 | 124580.1386 | 16841.3891 | 15631.8412 | 2852.811 | 122.1737 | 22.2967 | 44.3646 | 8.0965 | 9632.1782 | 3210.7261 | 3345.0156 | 3345.0156 | 557.5026 | 557.5026 | 965626.6956 | 279394.6963 | 1245021.3919 | 22735.8753
100 | 944.1832 | 644.1832 | 1015.9827 | 71.7995 | 731.5075 | 284.4752 | 731.5075 | 570.5759 | 160.9317 | 0 | 855.051 | 2433.3564 | 479 | 2438.0661 | 1600 | 2500 | 7272.7273 | 545.6654 | 62199.9291 | 85509.7011 | 124399.8582 | 16817.0179 | 15609.2203 | 2848.6827 | 122.0792 | 22.2795 | 44.3117 | 8.0869 | 9624.7233 | 3208.2411 | 3342.4267 | 3342.4267 | 557.0711 | 557.0711 | 964879.3445 | 279178.4576 | 1244057.802 | 22702.9741
Average | 1015.8748 | 715.8748 | 1094.8772 | 79.0024 | 788.3116 | 306.5656 | 788.3116 | 614.8831 | 173.4286 | 0 | 921.4487 | 2555.6578 | 479 | 2551.5312 | 1600 | 2500 | 7272.7273 | 545.6654 | 70321.6415 | 94088.1149 | 140643.283 | 19012.8883 | 17647.3834 | 3220.6475 | 131.5591 | 24.0095 | 49.6125 | 9.0543 | 10372.1161 | 3457.372 | 3601.9777 | 3601.9777 | 600.3296 | 600.3296 | 1039805.5396 | 300857.6237 | 1340663.1633
Max | 1189.094 | 889.094 | 1285.2425 | 96.1485 | 925.3746 | 359.8679 | 925.3746 | 721.7922 | 203.5824 | 0 | 1081.6601 | 2811.4486 | 479 | 2788.1493 | 1600 | 2500 | 7272.7273 | 545.6654 | 89982.7373 | 114508.2963 | 179965.4745 | 24328.666 | 22581.3822 | 4121.1022 | 154.4331 | 28.184 | 62.4027 | 11.3885 | 12175.5061 | 4058.502 | 4228.2501 | 4228.2501 | 704.7083 | 704.7083 | 1220595.534 | 353167.4509 | 1573762.9849
Annual Total |  |  | 49490202805.5687 | [16 empty] | 2953425927.5988 | 12095322.3399 | 1635108.3904 | 1517674.9698 | 276975.682 | [13 empty] | 2207396.327
Notes:
Max flow used for sizing capital equipment; annual flows used for OPEX | [5 empty] | Values for HDS sludge, lime, etc. directly from Updated Chino Mixing v3 1 0leach_TS_REV07192016 (003).xlsx
Flow values directly from Copy of Combined Flow and Water Quality to Treatment_04082019.xlxs | [5 empty] | Others values were extrapolated and/or calculated
28% | Membrane Bypass |  | Assuming 1600 mg/L SO4 in HDS Effluent, 20 mg/L SO4 in Perm
78% | RO Recovery
4.5455 | Brine Concentration Factor
300 | Interceptor Flow (gpm)
0.70469

## Sheet1 (hidden)
Main Pit Sulfate1 | Main Pit TDS1
(mg/l) | (mg/l)
24500 | 35700 | 1.4571
24500 | 35700 | 1.4571
24500 | 35700 | 1.4571
24500 | 35700 | 1.4571
24500 | 35700 | 1.4571
24500 | 35700 | 1.4571
24500 | 35700 | 1.4571
24500 | 35700 | 1.4571
24500 | 35700 | 1.4571
21028.6667 | 30593.5 | 1.4548
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
3672 | 5061 | 1.3783
3669.2571 | 5057.4857 | 1.3783
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
3576 | 4938 | 1.3809
3574.96 | 4936.62 | 1.3809
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! | #VALUE!
3524 | 4869 | 1.3817
3322 | 3322 | 1
3322 | 3322 | 1
3322 | 3322 | 1
3322 | 3322 | 1
3322 | 3322 | 1
3322 | 3322 | 1
3322 | 3322 | 1
3322 | 3322 | 1
3322 | 3322 | 1
3322 | 3322 | 1
3322 | 3322 | 1
3322 | 3322 | 1

## TTS Analytical Costs
Date: |  | REV 0 July 29, 2019
Project No.: |  | 18106417
Subject: |  | Analytical Costs
Project Short Title: |  | Tyrone Mine Closure Closeout Plan
Year | Seep/Interceptor System and NPDES Collection Points |  |  | Stockpile Location |  |  | Pit Location |  |  | Plant Performance | Number of total Samples | Cost per Sample | Total Cost Estimation | Cost per sample | Total Cost Estimation
| Quarterly | Semiannual | Annual | Quarterly | Semiannual | Annual | Quarterly | Semiannual | Annual | Monthly |  |  |  | Year | Year
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
1 | 2 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 8 | 47000 | 5875 | 403 | 3224
2 | 2 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 8 |  | 0 | 403 | 3224
3 | 2 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 8 |  | 0 | 403 | 3224
4 | 2 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 8 |  | 0 | 403 | 3224
5 | 2 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 8 | 53000 | 6625 | 403 | 3224
6 | 2 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 8 |  | 0 | 403 | 3224
7 | 2 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 8 |  | 0 | 403 | 3224
8 | 2 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 8 |  | 0 | 403 | 3224
9 | 2 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 8 |  | 0 | 403 | 3224
10 | 2 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 8 | 48000 | 6000 | 403 | 3224
11 | 2 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 8 |  | 0 | 403 | 3224
12 | 2 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 8 |  | 0 | 403 | 3224
13 | 0 | 2 | 0 |  |  |  | 0 | 0 | 0 | 0 | 4 |  | 0 | 403 | 1612
14 | 0 | 2 | 0 |  |  |  | 0 | 0 | 0 | 0 | 4 |  | 0 | 403 | 1612
15 | 5 | 2 | 0 |  |  |  | 4 | 0 | 0 | 3 | 76 | 31000 | 407.8947 | 403 | 30628
16 | 5 | 2 | 0 |  |  |  | 4 | 0 | 0 | 3 | 76 |  | 0 | 403 | 30628
17 | 5 | 2 | 0 |  |  |  | 4 | 0 | 0 | 3 | 76 |  | 0 | 403 | 30628
18 | 5 | 2 | 0 |  |  |  | 4 | 0 | 0 | 3 | 76 |  | 0 | 403 | 30628
19 | 5 | 2 | 0 |  |  |  | 4 | 0 | 0 | 3 | 76 |  | 0 | 403 | 30628
20 | 5 | 2 | 0 |  |  |  | 4 | 0 | 0 | 3 | 76 |  | 0 | 403 | 30628
21 | 5 | 2 | 0 |  |  |  | 4 | 0 | 0 | 3 | 76 |  | 0 | 403 | 30628
22 | 5 | 2 | 0 |  |  |  | 4 | 0 | 0 | 3 | 76 |  | 0 | 403 | 30628
23 | 5 | 2 | 0 |  |  |  | 4 | 0 | 0 | 3 | 76 |  | 0 | 403 | 30628
24 | 5 | 2 | 0 |  |  |  | 4 | 0 | 0 | 3 | 76 |  | 0 | 403 | 30628
25 | 5 | 2 | 0 |  |  |  | 4 | 0 | 0 | 3 | 76 | 18000 | 236.8421 | 403 | 30628
26 | 5 | 2 | 0 |  |  |  | 4 | 0 | 0 | 3 | 76 |  | 0 | 403 | 30628
27 | 5 | 2 | 0 |  |  |  | 4 | 0 | 0 | 3 | 76 |  | 0 | 403 | 30628
28 | 5 | 2 | 0 |  |  |  | 4 | 0 | 0 | 3 | 76 |  | 0 | 403 | 30628
29 | 5 | 2 | 0 |  |  |  | 4 | 0 | 0 | 3 | 76 |  | 0 | 403 | 30628
30 | 5 | 2 | 0 |  |  |  | 4 | 0 | 0 | 3 | 76 |  | 0 | 403 | 30628
31 | 5 | 2 | 0 |  |  |  | 4 | 0 | 0 | 3 | 76 |  | 0 | 403 | 30628
32 | 5 | 2 | 0 |  |  |  | 4 | 0 | 0 | 3 | 76 | 18000 | 236.8421 | 403 | 30628
33 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
34 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
35 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
36 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
37 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
38 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
39 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
40 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 | 18000 | 382.9787 | 403 | 18941
41 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
42 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
43 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
44 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
45 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
46 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
47 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
48 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
49 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
50 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
51 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
52 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
53 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
54 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
55 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
56 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
57 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
58 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
59 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
60 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
61 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
62 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
63 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
64 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
65 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
66 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
67 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
68 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
69 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
70 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
71 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
72 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
73 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
74 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
75 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
76 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
77 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
78 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
79 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
80 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
81 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
82 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
83 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
84 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
85 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
86 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
87 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
88 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
89 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
90 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
91 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
92 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
93 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
94 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
95 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
96 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
97 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
98 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
99 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 |  | 0 | 403 | 18941
100 | 0 | 0 | 7 |  |  |  | 0 | 0 | 4 | 3 | 47 | 0 | 0 | 403 | 18941
[14 empty] | TOTAL | 1881204
Notes:
Costs do not include indirect costs
The frequency of sampling and analysis associated with the water management and treatment system is as follows:
Sampling is not required as part of the O&M of the short-term ETS. The only sampling required during the short-term ETS operational period is associated with the NPDES compliance points (two associated with NPDES Permit NMR05GB76).
The high TDS and sulfate water sources will not need to be sampled as part of the O&M for the long-term ETS.
TTS performance monitoring including (2) influent and (1) effluent discharge from water treatment plant: monthly beginning in Year 15 and continuing though Year 100.
NPDES compliance points: quarterly from Year 1 through Year 12, semiannual from Year 13 through Year 32, and annual thereafter (through Year 100).
Collection points for the low TDS and sulfate non-process water streams to the TTS (1X1 Pond, 1A PLS Tank, 1B PLS Tank, Oak Grove Pond, and New No. 3 AST): quarterly from Year 15 through Year 32 (transition period between uncovered and covered flows), and annual thereafter (through Year 100).
Discharge from groundwater interceptor system (4 interceptor wells): quarterly from Year 15 through Year 32 (transition period between uncovered and covered flows), and annual thereafter (through Year 100). The groundwater interceptor system will be sampled at the point that all 4 wells are combined into one pipeline.
Pits (4 sample points-Main Pit, Gettysburg Pit, Copper Mountain Pit, Savanna Pit): quarterly from Year 15 through Year 32 (transition period between uncovered and covered flows), and annual thereafter (through Year 100).

## TTS O&M Input
Date: | REV 0 July 29, 2019
Project No.: | 18106417
Subject: | TTS O&M Cost Inputs
Project Short Title: | Tyrone Mine Closure Closeout Plan
Reagent Inputs
Lime (CaO) ($/ton) | = | 256 | 2019 Lhoist Cost (Freight Estimated)
Flocculent ($/lb) | = | 3.36 | 2019 NALCO Water
Hydrochloric Acid - 35% ($/lb) | = | 0.21 | 2019 Univar Mining - HCl (35%) from bulk delivery (tote price $0.335/lb)
MF High pH Cleaning Chemicals ($/lb) | = | 3.53 | 2019 Avista quote - pail price (assume bimonthly cleaning during high flows)
MF Low pH Cleaning Chemicals ($/lb) | = | 3.53 | 2019 Avista quote - pail price (assume bimonthly cleaning during high flows)
RO High pH Cleaning Chemicals ($/lb) | = | 7.52 | 2019 Avista quote - pail price (assume quarterly cleaning during high flows)
RO Low pH Cleaning Chemicals ($/lb) | = | 6.44 | 2019 Avista quote - pail price (assume quarterly cleaning during high flows)
Biocide ($/lb) | = | 8.15 | 2019 Avista quote - tote price
Antiscalant ($/lb) | = | 3.09 | 2019 Avista quote - tote price
Electricity Input
Electricity ($/kwh) | = | 0.044694 | PNM Method of Calculation (Avg ($/kWh) Years 1 through 14) using 2019 PNM Rate Schedule | https://www.dws.state.nm.us/Portals/0/DM/LaborRelations/Prevailing_Wage_Poster_H_2019_final.pdf
| = | 0.045334 | PNM Method of Calculation (Avg ($/kWh) Years 15 through 100) using 2019 PNM Rate Schedule
Analytical Input
Analytical Cost ($/sample) | = | 403 | 2019 Hall Environmental Analysis Laboratory (price unchanged from 2018, quote changed to be valid through 2019)
Labor Inputs |  |  | NOTE - Type A schedule used for operating labor and Type H schedule used for construction labor
Operator Base Rate | = | 18.6 | 2019 NM Type "A" Street, Highway, Utility & Light Engineering Prevailing Wages. Operator Group I. (1)
Supervisor Rate | = | 31.1 | 2019 NM Type "A" Street, Highway, Utility & Light Engineering Prevailing Wages. Operator Group X. (1)
Maintenance Technician Rate | = | 19.83 | 2019 NM Type "A" Street, Highway, Utility & Light Engineering Prevailing Wages. Operator Group V. (1)
Operator Fringe Rate | = | 5.94 | 2019 NM Type "A" Street, Highway, Utility & Light Engineering Prevailing Wages. Applies to operator groups I, X, V under Type A. (1)
Laborer (Group II) | = | 23.84 | 2019 NM Department of Labor Type H (Heavy Engineering) 2019 labor rates. Rates include base hourly wage, fringe benefit, and apprenticeship contribution rates. (2)
Plumber/Pipefitter | = | 45.45 | 2019 NM Department of Labor Type H (Heavy Engineering) 2019 labor rates. Rates include base hourly wage, fringe benefit, and apprenticeship contribution rates. (2)
Electrician (Lineman/Tech Outside) | = | 55.13 | 2019 NM Department of Labor Type H (Heavy Engineering) 2019 labor rates. Rates include base hourly wage, fringe benefit, and apprenticeship contribution rates. (2)
Electrician (Wireman/Tech Inside) | = | 54.054 | 2019 NM Department of Labor Type H (Heavy Engineering) 2019 labor rates. Rates include base hourly wage, fringe benefit, and apprenticeship contribution rates. Includes 26% increase for work outside Zone 1. (2)
Ironworker | = | 48.66 | 2019 NM Department of Labor Type H (Heavy Engineering) 2019 labor rates. Rates include base hourly wage, fringe benefit, apprenticeship contribution rates, and subsistence rate. (2)
Maintenance
Replacement O&M | = | 1.5% | of Direct Capital Cost
Routine Maintenance | = | 1.5% | of Direct Capital Cost
Per Diem Subsistence, Zone and Incentive | = | 50 | per day for Plumber/Pipefitter, Electrical Lineman/Tech (outside). 2019 NM Department of Labor Type H (Heavy Engineering), 2019 Subsistence, Zone, and Incentive Pay Rates
2019 Subsistence, Zone and Incentive Pay Rates, per diem only required for Electrician (Outside classification) and Plumber/Pipefitters for the construction labor classes used for TTS construction. Operating labor is assumed to be local
Notes:
(1) - https://www.dws.state.nm.us/Portals/0/DM/LaborRelations/Prevailing_Wage_Poster_A_2019_final.pdf
(2) - https://www.dws.state.nm.us/Portals/0/DM/LaborRelations/Prevailing_Wage_Poster_H_2019_final.pdf

## TTS Design Calcs
Date: | REV 0 July 29, 2019
Project No.: | 18106417
Subject: | Example Calculations
Project Short Title: | Tyrone Mine Closure Closeout Plan
Flow and Sulfate Inputs
Max Year | = | 6
Membrane Max Flow rate | = | 1300 | gpm
Membrane Avg Flow rate | = | 800 | gpm
HDS Equipment Max Flow rate | = | 1600 | gpm
HDS Equipment Avg Flow rate | = | 1100 | gpm
HDS Sulfate Max | = | 2788.1493 | mg/L
HDS Sulfate Avg | = | 2551.5312 | mg/L
Sludge Recycle Avg Flow rate | = | 79.0024 | gpm
Sludge Max (50% Solids) | = | 179965.4745 | lb/day
Sludge Avg (50% Solids) | = | 140643.283 | lb/day
Effluent Neutralization Max (if necessary) | = | 1100 | gpm
Effluent Neutralization Avg Flow rate(if necessary) | = | 1000 | gpm
Equipment sizing based on maximum flows, operating costs based on average flows.
Van Riper Study (2002) Inputs
Lime Consumption Factor | = | 0.5249 | mg/L CaO/mg/L SO4 | 5,270 mg/L CaO needed to treat high metals AMD water with sulfate concentration of 10,040 mg/L
Sulfuric Acid Consumption Factor | = | 2.8e-05 | lb/gal | 0.028 pounds per 1,000 gallons (50 mg acid per liter of water treated)
Sludge Factor | = | 2.0916 | mg/L Sludge/mg/L SO4 | 21,000 mg/L Sludge for 10,040 mg/L SO4
Van Riper treatability study results used to detemine lime usage and sludge production according to the factors listed above and the sulfate concentration.
HDS Chemical Precipitation
Reaction Tank
Tank size | = | 1600 | gal | x | 24 | min
Need 4 reaction tanks - to provide minimum of 90 |  | 1 | min
min retention time at max flow and minimum of 120 min | = | 38400 | gal
retention time at avg flow
| = | 38400 | gal | x | 1.1 | Freeboard
|  | 1 | min
| = | 43000 | gal | each tank, total of 4 tanks for approximately 90 min reaction time
| = | 43000 | gal | x | 1 | ft3
[5 empty] | 7.481 | gal
| = | 5747.8947 | ft3
Tank Height | = | 20 | ft
Diameter | = | 5747.8947 | ft3 | x | 4 | 0.5
|  | 20 | ft |  | π
| = | 20 | ft
Mixing Requirement | = | 0.001139 | N-s | x | 5747.8947 | ft3 | x | 1 | m3 | x |  | W | x | 300 |  | 2
|  |  | m2 |  |  |  |  | 35.3 | ft3 |  | 1000 | kW |  | 1 | sec
| = | 17 | kW
Floc Tank
Tank size | = | 1600 | gal | x | 3.5 | min
|  | 1 | min
| = | 5600 | gal
| = | 5600 | gal | x | 1.1 | Freeboard
|  | 1 | min
| = | 7000 | gal
| = | 7000 | gal | x | 1 | ft3
[5 empty] | 7.481 | gal
| = | 935.7038 | ft3
Tank Height | = | 12 | ft
Diameter | = | 935.7038 | ft3 | x | 4 | 0.5
|  | 12 | ft |  | π
| = | 10 | ft
Mixing Requirement | = | 0.001139 | N-s | x | 935.7038 | ft3 | x | 1 | m3 | x |  | W | x | 300 |  | 2
|  |  | m2 |  |  |  |  | 35.3 | ft3 |  | 1000 | kW |  | 1 | sec
| = | 3 | kW
Clarifier
Tank size (based on Clarification) | = | 1600 | gal | x | 1 | ft2
Use conservative loading rate of 0.3 gpm/ft2 |  | 1 | min |  | 0.295 | gpm
considering sludge is primarily calcium sulfate and | = | 5423.7288 | ft2
iron hydroxide and densified.
Diameter (based on Clarification) | = | 5423.7288 | ft2 | x | 4 | 0.5
π
| = | 84 | ft
Depth (based on Clarification) | = | 15 | ft
Overflow
Solids underflow | = | 405511.0359 | lb | x | 1 | kg | x | 1 | day | x | 1 | m3 | x | 264.2 | gal
|  |  | day |  | 2.2 | lb |  | 1440 | min |  | 1190 | kg |  | 1 | m3
| = | 29 | gpm
Solids recycle (max) | = | 3 | Recycles | x | 179965.4745 | lb | x |  |  | x | 1 | gal | x |  |  | x | 1 | day
(assumption) | [5 empty] | d |  | 25% | solids |  | 8.34 | lb |  | 1.19 | SG |  | 1440 | min
| = | 152 | gal/min
Effluent Neutralization System
Effluent Neutralization Tank
Tank size | = | 1100 | gal | x | 18 | min
|  | 1 | min
| = | 19800 | gal
| = | 19800 | gal | x | 1.1 | Freeboard
|  | 1 | min
| = | 22000 | gal
| = | 22000 | gal | x | 1 | ft3
[5 empty] | 7.481 | gal
| = | 2940.7833 | ft3
Tank Height | = | 20 | ft
Diameter | = | 2940.7833 | ft3 | x | 4 | 0.5
|  | 20 | ft |  | π
| = | 14 | ft
Mixing Requirement | = | 0.001139 | N-s | x | 2940.7833 | ft3 | x | 1 | m3 | x |  | W | x | 300 |  | 2
|  |  | m2 |  |  |  |  | 35.3 | ft3 |  | 1000 | kW |  | 1 | sec
| = | 9 | kW
Discharge System
Discharge Tank
Tank size | = | 1100 | gal | x | 30 | min
|  | 1 | min
| = | 33000 | gal
| = | 33000 | gal | x | 1.1 | Freeboard
|  | 1 | min
| = | 37000 | gal
| = | 37000 | gal | x | 1 | ft3
[5 empty] | 7.481 | gal
| = | 4945.8629 | ft3
Tank Height | = | 20 | ft
Diameter | = | 4945.8629 | ft3 | x | 4 | 0.5
|  | 20 | ft |  | π
| = | 18 | ft
Solids Management
Sludge Storage Tank
Sludge Production | = | 21000 | mg Sludge | x | 1 | L
per Hazen Research, Inc., May 3, 2002 |  | 1 | L |  | 10040 | mg SO4
Van Riper Factor (Sulfate x Factor = sludge) | = | 2.0916 | mg/L
Influent Concentration | = | 2788.1493 | mg SO4 | x | 2.0916 | mg/L Sludge
|  | 1 | L |  | 1 | mg/L SO4
| = | 5831.7863 | mg/L
Influent Dry Solids | = | 5831.7863 | mg | x | 1448 | gal | x | 3.785 | L | x | 1440 | min | x | 1 | lb
|  | 1 | L |  | 1 | min |  | 1 | gal |  | 1 | d |  | 454000 | mg
| = | 101377.759 | lb/day
Influent Wet Cake | = | 101377.759 | lb | x | 1 | Wet Cake
|  | 1 | day |  | 50% | Dry Solids
|  | 202755.5179 | lb/day
Influent Wet Solids | = | 101377.759 | lb/day | x | 1 | Wet Solids
(Clarifier Underflow) |  | 1 | day |  | 25% | Wet Cake
|  | 405511.0359 | lb/day
Water Content | = | 405511.0359 | lb | - | 202755.5179 | lb
(filtrate from dewatering) |  | 1 | day |  | 1 | day
|  | 202755.5179 | lb/day
| = | 202755.5179 | lb | x | 1 | kg | x | 1 | m3 | x | 1 | day | x | 264.2 | gal
|  | 1 | day |  | 2.2 | lb |  | 1000 | kg |  | 1440 | min |  | 1 | m3
|  | 16.9091 | gpm
Volume of Cake - Max | = | 202755.5179 | lb | x | 1 | ft3 | x | 365 | days
|  | 1 | day |  | 100 | lb |  | 1 | yr
|  | 740057.6404 | ft3/yr
Filter Press Size - Max | = | 740057.6404 | ft3 | x | 1 | yr | x | 1 | days | x | 1 | cycle
|  | 1 | yr |  | 365 | days |  | 6 | cycle |  | 3 | filter presses online |  |  | 2 shifts, 3 presses |  |  | 6 | op
|  | 100 | ft3/cycle/filter press
Volume of Cake - Average | = | 140643.283 | lb | x | 1 | ft3 | x | 365 | days
|  | 1 | day |  | 100 | lb |  | 1 | yr
|  | 513347.983 | ft3/yr
Filter Press Size - Avg | = | 513347.983 | ft3 | x | 1 | yr | x | 1 | days | x | 1 | cycle |  |  | 1 shift 3 presses
|  | 1 | yr |  | 365 | days |  | 3 | cycle |  | 3 | filter presses online
|  | 200 | ft3/cycle/filter press
Sludge storage tank | = | 29 | gal | x | 270 | min | x | 1.1 | Freeboard
|  | 1 | min
| = | 9000 | gal
| = | 9000 | gal | x | 1 | ft3
[5 empty] | 7.481 | gal
| = | 1203.0477 | ft3
Tank Height | = | 12 | ft
Diameter | = | 1203.0477 | ft3 | x | 4 | 0.5
|  | 12 | ft |  | π
| = | 12 | ft
Filtrate Tank
Filtrate | = | 9 | gpm
Tank size | = | 9 | gal | x | 240 | min
|  | 1 | min
| = | 3000 | gal
| = | 3000 | gal | x | 1 | ft3
[5 empty] | 7.481 | gal
| = | 401.0159 | ft3
Tank Height | = | 10 | ft
Diameter | = | 401.0159 | ft3 | x | 4 | 0.5
|  | 10 | ft |  | π
| = | 8 | ft
Chemical Addition Systems
Lime Chemical Addition System
Lime Consumption | = | 5270 | mg CaO | x | 1 | L
per Hazen Research, Inc., May 3, 2002 |  | 1 | L |  | 10040 | mg SO4
| = | 0.5249 | mg/L CaO / mg/L SO4
Lime, CaO | = | 2788.1493 | mg SO4 | x | 0.5249 | mg/L CaO
|  | 1 | L |  | 1 | mg/L SO4
| = | 1463.5007 | mg/L CaO
Lime Consumption | = | 1463.5007 | mg CaO | x | 3.785 | L | x | 1 | lb | x | 1448 | gal | x | 1440 | min
|  | 1 | L |  | 1 | gal |  | 454000 | mg |  | 1 | min |  | 1 | day
| = | 25440.99 | lb CaO/day
Volume, 10% Ca(OH)2 slurry | = | 25440.99 | lb | x | 1 | kg | x | 1 | L | x | 1 | day | x | 1 | Concentration | x | 1 |  | x | 1 | gal | x | 75 | mg CaOH2
From FMI's Calcs |  | 1 | day |  | 2.2 | lb |  | 1 | kg |  | 1440 | min |  | 10% | Factor |  | 1.07 | SG |  | 3.785 | L |  | 56 | mg CaO
| = | 27 | gpm
Lime Consumption, as CaO | = | 25441 | lb CaO | x | 1 | day | x | 1 | min
|  | 1 | day |  | 1440 | min |  | 1600 | gal
| = | 0.011042 | lb CaO/gal
Chemical Usage, as CaO | = | 25441 | lbs CaO | x | 365 | day | x | 1 | ton
|  | 1 | day |  | 1 | yr |  | 2000 | lbs
| = | 4643 | ton CaO/yr
Densification Tank (lime slurry + recycled sludge) | = | 179 | gpm
Tank size | = | 179 | gal | x | 5 | min
|  | 1 | min
| = | 900 | gal
| = | 900 | gal | x | 1 | ft3
[5 empty] | 7.481 | gal
| = | 120.3048 | ft3
Tank Height | = | 6 | ft
Diameter | = | 120.3048 | ft3 | x | 4 | 0.5
|  | 6 | ft |  | π
| = | 6 | ft
Flocculent Chemical Addition System
Mass | = | 10 | mg | x | 3.785 | L | x | 1600 | gal | x | 1 | lb
Estimated from experience |  | 1 | L |  | 1 | gal |  |  | min |  | 453600 | mg
(typically moderately anionic polymer) | = | 0.13351 | lb/min
Usage | = | 0.13351 | lb | x |  |  | x | 1440 | min | x | 365 | d
|  | 1 | min |  | 1600 | gpm |  | 1 | d |  | 1 | yr
| = | 43.8579 | lb/yr-gpm
Volume | = | 0.13351 | lb | x | 1 | kg | x | 1 | L | x | 60 | min | x | 1 | Concentration | x | 1 |  | x | 1 | gal
|  | 1 | min |  | 2.2 | lb |  | 1 | kg |  | 1 | hr |  | 100% | Factor |  | 1 | SG |  | 3.785 | L
| = | 0.97 | gph
HCl Acid Chemical Addition
NOTE: 2018 UPDATE INCLUDES USING HCL INSTEAD OF SULFURIC - THE FOLLOWING CONVERSION FACTOR IS INCORPORATED INTO THE SUMMARY SHEET TO CONVERT 93% SULFURIC USAGE TO 35% HCL USAGE
| = | 1 | lb 93% H2SO4 | x | 93 | lb H2SO4 | x | 1 | mol H2SO4 | x | 2 | mols H+ | x | 1 | mol HCl | x | 36.46 | lb HCl | x | 100 | lb 35%
|  | 1 | gal |  | 100 | lb 93% |  | 98 | lb H2SO4 |  | 1 | mol H2SO4 |  | 1 | mol H+ |  | 1 | mol HCl |  | 35 | lb HCl
factor lb SO4(93%)/gal to lb HCl (35%)/gal |  | 1.9771 | lb 35%HCL/gal
HCl (35%) Acid Consumption | = | 0.028 | lbs H2SO4 (93%) | x | 1.98 | lbs HCl (35%)
Used Van Riper Consulting, 2002 for H2SO4 |  | 1000 | gal |  | 1 | lbs H2SO4 (93%)
then converted to 35% HCl | = | 5.544e-05 | lbs/gal
Mass | = | 5.544e-05 | lbs | x | 453600 | mg | x | 1 | gal
|  | 1 | gal |  | 1 | lb |  | 3.785 | L
| = | 6.65 | mg/L
Usage | = | 6.65 | mg | x | 1100 | gal | x | 3.785 | L | x | 1 | lb
|  | 1 | L |  | 1 | min |  | 1 | gal |  | 453600 | mg
| = | 0.061039 | lb/min
Volume | = | 0.061039 | lb | x | 1 | kg | x | 1 | L | x | 60 | min | x | 1 | Concentration | x | 1 |  | x | 1 | gal
|  | 1 | min |  | 2.2 | lb |  | 1 | kg |  | 1 | hr |  | 35% | Factor |  | 1.18 | SG |  | 3.785 | L
| = | 1.07 | gph
Chemical Usage | = | 5.544e-05 | lbs | x | 1100 | gal | x | 1440 | min | x | 365 | day
|  | 1 | gal |  | 1 | min |  | 1 | day |  | 1 | yr
| = | 32053.1904 | lbs/yr
MF Cleaning Chemicals
High pH Cleaner Mass | = | 2 | cleanings | x | 12 | month | x | 5.5 | pail | x | 45 | lb
Estimated from experience |  | 1 | month |  | 1 | yr |  |  | cleaning |  |  | pail
and advice from Avista | = | 5940 | lb/yr
High pH Cleaner Usage Rate | = | 5940 | lb MF Cleaning Chem | x
|  | 1 | year |  | 1300 | gpm
| = | 4.5692 | lb/yr-gpm
Low pH Cleaner Mass | = | 2 | cleanings | x | 12 | month | x | 5.5 | pail | x | 45 | lb
Estimated from experience |  | 1 | month |  | 1 | yr |  |  | cleaning |  |  | pail
and advice from Avista | = | 5940 | lb/yr
Low pH Cleaner Usage Rate | = | 5940 | lb MF Cleaning Chem | x
|  | 1 | year |  | 1300 | gpm
| = | 4.5692 | lb/yr-gpm
RO Cleaning Chemicals
High pH Cleaner Mass | = | 1 | cleanings | x | 12 | month | x | 5.5 | pail | x | 45 | lb
Estimated from experience |  | 3 | month |  | 1 | yr |  |  | cleaning |  |  | pail
and avista advice | = | 990 | lb/yr
High pH Cleaner Usage Rate | = | 990 | lb MF Cleaning Chem | x
|  | 1 | year |  | 1300 | gpm
| = | 0.76154 | lb/yr-gpm
Low pH Cleaner Mass | = | 1 | cleanings | x | 12 | month | x | 5.5 | pail | x | 45 | lb
Estimated from experience |  | 3 | month |  | 1 | yr |  |  | cleaning |  |  | pail
| = | 990 | lb/yr
Low pH Cleaner Usage Rate | = | 990 | lb MF Cleaning Chem | x
|  | 1 | year |  | 1300 | gpm
| = | 0.76154 | lb/yr-gpm
Antiscalant
Mass | = | 3 | mg | x | 3.785 | L | x | 1300 | gal | x | 1 | lb | x | 1440 | min | x | 365 | d
Estimated from experience |  | 1 | L |  | 1 | gal |  |  | min |  | 453600 | mg |  |  | d |  | 1 | yr
| = | 17104.5952 | lb/yr
Usage | = | 17104.5952 | lb MF Cleaning Chem | x
|  | 1 | year |  | 1300 | gpm
| = | 13.1574 | lb/yr-gpm
Biocide
Mass | = | 1 | mg | x | 3.785 | L | x | 1300 | gal | x | 1 | lb | x | 1440 | min | x | 365 | d
Estimated from experience |  | 1 | L |  | 1 | gal |  |  | min |  | 453600 | mg |  |  | d |  | 1 | yr
| = | 5701.5317 | lb/yr
Usage | = | 5701.5317 | lb | x
|  | 1 | yr |  | 1300 | gpm
| = | 4.3858 | lb/yr-gpm
Process Water (Does not include slaking water)
Water required | = | Polymer make-down |  | + | Lime make-down
| = | 0.97 | gal | + | 27 | gal
|  |  | min |  |  | min
Water required | = | 27.97 | gpm
Tank size | = | 27.97 | gal | x | 75 | min
|  | 1 | min
| = | 3000 | gal
| = | 3000 | gal | x | 1 | ft3
[5 empty] | 7.481 | gal
| = | 401.0159 | ft3
Tank Height | = | 10 | ft
Diameter | = | 401.0159 | ft3 | x | 4 | 0.5
|  | 10 | ft |  | π
| = | 8 | ft
Power Consumption
Membrane System | = | 262.5 | hp | x | 0.7457 | kw | x | 24 | hr | x | 365 | day
Plus 5% for building load |  |  |  |  | 1 | hp |  | 1 | day |  | 1 | year
| = | 1714737.15 | kw-hr/year
| = | 1714737.15 | kw-hr | x
|  |  | year |  | 1300 | gpm
|  | 1319.0286 | kw-hr/gpm-yr
HDS System | = | 67.305 | hp | x | 0.7457 | kw | x | 24 | hr | x | 365 | day
Plus 5% for building load |  |  |  |  | 1 | hp |  | 1 | day |  | 1 | year
| = | 439658.6053 | kw-hr/year
| = | 439658.6053 | kw-hr | x
|  |  | year |  | 1600 | gpm
|  | 274.7866 | kw-hr/gpm-yr
Note on F153: Hendricks, Bridgette: Note that the sizing of the HDS equipment takes into account the flow from the NMA raw water, the sludge recycle, and the brine recycle, however, the sulfate load is not attributed to the sludge recycle.

## TTS Labor
Date: | REV 0 July 29, 2019
Project No.: | 18106417
Subject: | Labor Cost Estimate - TTS and SDF Operations
Project Short Title: | Tyrone Mine Closure Closeout Plan
Year 15 Solids | Max Solids - All 3 shifts1 | Max Solids - All 3 shifts1 |  | Max Solids - All 3 shifts1 | Max Solids - All 3 shifts1
Day shift - 1 supervisor, 2 maintenance - 40 hrs a week (also used for ETS, SDF, Salt Disposal Facility) Operators at 6 Per shift as follows - 2 filter press, 1 lime silo, 1 membrane, 1 HDS, 1 pumps/pipelines (conveyance and discharge) and ETS. 2 shifts each 8 hr days, 7 days week, Covered by 2 crews that work full-time 8 hr shifts 5 days per week (one crew on days and one on evenings). Assumes 2 crews on weekends both working part-time hours to cover the 2 8-hour shifts per day on weekends. |  |  | Note that the sludge falls by 10% from year 15 to year 25 so at year 25% a 10% deduction is taken on the total labor cost. At Year 43 the sludge decreases another 10% so another 10% decrease in annual labor cost is included at year 43 and again at year 92.
Operators2 | 16.8 |  | Operators | 16.8
Operator Rate2 | 18.6 | /hr | Operator Rate | 18.6 | /hr
Reg Operator Hours 2 | 2087 | hr/op | Operator Hours | 2087 | hr/op
Operator Total Cost | 652145.76 |  | Operator Total Cost | 652145.76
Supervisors | 1 |  | Supervisors | 1
Supervisor Rate3 | 31.1 | /hr | Supervisor Rate | 31.1 | /hr
Supervisor Hours (5 day/wk) | 2087 | hr/op | Supervisor Hours | 2087 | hr/op
Supervisor Total Cost | 64905.7 |  | Operator Total Cost | 64905.7
Maintenance Techs | 2 |  | Maintenance Techs | 2
Maintenance Tech Rates4 | 19.83 | /hr | Maintenance Tech Rates | 19.83 | /hr
Maintenance Tech Hours (5 day/wk) | 2080 | hr/op | Maintenance Tech Hours | 2080 | hr/op
Maintenance Tech Total Cost | 82492.8 |  | Maintenance Tech Total Cost | 82492.8
Sub-Total Labor Cost | 799544.26 |  | Sub-Total Labor Cost | 799544.26
Overtime for supervisor5 | 10% |  | Overtime for supervisor5 | 10%
Overtime hours for supervisor | 208.7 |  | Overtime hours for supervisor | 208.7
Supervisor Overtime Total Cost | 9735.855 |  | Supervisor Overtime Total Cost | 9735.855
Overtime for maintenance5 | 10% |  | Overtime for maintenance5 | 10%
Overtime hours for maintenance | 416 |  | Overtime hours for maintenance | 416
Maintenance Overtime Total Cost | 12373.92 |  | Maintenance Overtime Total Cost | 12373.92
Overtime for operators5 | 15% |  | Overtime for operators5 | 15%
Overtime hours for operators5 | 5259.24 |  | Overtime hours for operators5 | 5259.24
Operator Overtime Total Cost | 146732.796 |  | Operator Overtime Total Cost | 146732.796
Overtime Cost | 168842.571 |  | Overtime Cost | 168842.571
Benefits fringe rate per hour6 | 5.94 | /hr | Benefits fringe rate per hour6 | 5.94 | /hr
Number of employees | 19.8 | ops | Number of employees | 19.8 | ops
Hours per year | 2087 | hrs/op | Hours per year | 2087 | hrs/op
Benefits Cost | 245456.244 |  | Benefits Cost | 245456.244
Benefits Cost | 245456.244 |  | Benefits Cost | 245456.244
Total Labor Cost | 1213843.075 |  | Total Labor Cost | 1213843.075
Sludge (lb/day) | 179965.4745 |  | Sludge (lb/day) | 140643.283
Labor Cost/lb sludge ($/d) | 6.7449 |  | Labor Cost/lb sludge ($/d) | 8.6307
Notes:
1 Operator numbers are estimated from Golder's experience with operating similar plants.
2 Number of operators reflects covering 16 hours per day and 7 days per week with 2 shifts of 6 operators working 8 hours per day (day shift and evening shift) and 2 shifts of 6 operators working part-time on the weekends for 16 hours total (8 hours per day times two days) and covering the day shift and evening shift. This results in an equivalent number of full-time operators of 16.8 to cover 16 hours per day and 7 days per week. Rate per operators is from 2019 NM Type "A" Street, Highway, Utility & Light Engineering Prevailing Wages. Operator Group I. Hours per operator is regular hours to cover 6 operator positions for 16 hours per day (12 operators per day) 7 days per week (56 hrs/week x 7 days/week per operator position) . It is assumed that a shift of 40 hour per week operators and a shift of weekend 16 hour per week operators can be hired to staff the plant for a 8 hour per day shift and an 8 hour swing shift per day. This staffing plan assumes part-time operators are available. https://www.dws.state.nm.us/Portals/0/DM/LaborRelations/Prevailing_Wage_Poster_A_2019_final.pdf
3 Rate per operator is from 2019 NM Type "A" Street, Highway, Utility & Light Engineering Prevailing Wages. Operator Group X. https://www.dws.state.nm.us/Portals/0/DM/LaborRelations/Prevailing_Wage_Poster_A_2019_final.pdf.
4 2019 NM Type "A" Street, Highway, Utility & Light Engineering Prevailing Wages. Operator Group V. https://www.dws.state.nm.us/Portals/0/DM/LaborRelations/Prevailing_Wage_Poster_A_2019_final.pdf
5Overtime for supervisor/maintenance at 10% of regular time hours is for call-outs when off-shift (nights and weekends). Overtime for operators includes average of 15% for nightime callouts (midnight to 8 am), unexpected projects, covering sick time, holiday work, etc). Overtime rate for operators assumes "worst-case" situation and that the part-time weekend operators are not available to cover and the full-time operators must cover at the Overtime rate.
6 2019 NM Type "A" Street, Highway, Utility & Light Engineering Prevailing Wages. All Operator groups. https://www.dws.state.nm.us/Portals/0/DM/LaborRelations/Prevailing_Wage_Poster_A_2019_final.pdf
7

## Chino Tyrone Comparison (hidden)
Date: |  |  | 2019-05-14 | 2019-05-14
Project No.: |  |  | 18106417 | 18106417
Subject: |  |  | O&M Quantity Comparison Summary Table | O&M Quantity Comparison Summary Table
Project Short Title: |  |  | Chino Mine Closure Closeout Plan | Chino Mine Closure Closeout Plan
Comparison of Chino and Tyrone
Indirect | Units | Chino | Tyrone with recycle | Tyrone with evaporation
Membrane Max Flow rate | gpm | 1400 | 1000 | 1000
Membrane Avg Flow rate | gpm | 700 | 900 | 900
HDS Equipment Max Flow rate | gpm | 1100 | 1300 | 1300
HDS Equipment Avg Flow rate | gpm | 620 | 1110 | 1110
HDS Sulfate Max | mg/L | 6858.3935 | 3617.02 | 3617.02
HDS Sulfate Avg | mg/L | 3636.384 | 3474.4895 | 3474.4895
Sludge Recycle Avg Flow rate | gpm | 123.5083 | 87.8577 | 87.8577
Sludge Max (50% Solids) | lb/day | 295452.9999 | 254847.6808 | 254847.6808
Sludge Avg (50% Solids) | lb/day | 108339.6112 | 209268.4926 | 209268.4926
Effluent Neutralization Max (if necessary) | gpm | 1500 | 1200 | 1200
Effluent Neutralization Avg Flow rate(if necessary) | gpm | 800 | 1100 | 1100
|  | 17063018.5443 | 19731217.7168 | 0
|  | 7559078.6871 | 15167714.9045 | 0
|  | 100303735.6607 | 242505014.0038 | 228629427.5135
|  | 6618316.1026 | 14211879.4806 | 0
|  | 0 | 0 | 0
|  | 0 | 0 | 0
|  | 131544148.9947 | 291615826.1056 | 228629427.5135
|  | 92080904296.2949 | 262454243495.069 | 205766484762.153
|  | 92212448445.2896 | 262745859321.175 | 205995114189.666
O&M Costs - Replacement O&M, Routine Maintenance, Labor
Short-Term ETS |  | 1336899.1725 | 382928414.0751 | 398834258.9469
Long-Term ETS |  | 6351324.2174 | 5184625.9574 | 15936420.7153
South Mine Area Water Treatment System (STS) |  | 105570872.2707 | 89565482.6892 | 94111215.1292
Water Collection/Conveyance for STS |  | 6633702.378 | 3700196.0324 | 149005782.7902
Sludge Disposal Facility for STS |  | 5142345.7835 | -183573.2153 | 0
Salt Disposal Facility for ETS |  | 7352254.9599 | -225230.0846 | 0
Subtotal, O&M Labor, Routine Maintenance |  | 132387398.7819 | 480969915.4541 | 657887677.5816
Indirect Costs, O&M Labor, Routine Maintenance |  | 92671179147.3138 | 432872923908.728 | 592098909823.454
Total, O&M Labor, Routine Maintenance |  | 92803566546.0956 | 433353893824.182 | 592756797501.035
Total, O&M |  | 185016014991.385 | 696099753145.3571 | 798751911690.701
Total, Capital and O&M in Current Costs |  | 185016014991.385 | 696099753145.3571 | 798751911690.701